# Fish Passage Plan (FPP) Change Request Form

**Change Form # & Title**: 19TDA004 – AWS Backup Operation 2

**Date Submitted**: 2/28/2019

**Project**: TDA

**Requester Name, Agency**: Bob Cordie, USACE

**Final Action:**

**FPP Section**: TDA 4.3.2.1.b.

**Justification for Change**: Newly constructed East fishway AWS backup system

**Proposed Change**: *[see below with edits to existing FPP in track changes]*

**4.3.2.1.b**. If both of the fishway auxiliary water turbines fail or malfunction, regardless of fish passage season, the adult passage facility will be operated as follows:

Open AWS backup water supply.

Raise the south entrance weirs to elevation 81’ msl (closed position).

Close west entrance.

Close entrance weir E1, and keep E2 and E3 at >8’ depth.

Operate closest available main unit to the east entrance for attraction flow.

**Comments**:

**Record of Final Action**: