Draft Comments on Change Forms for FPP

Attached are the Change forms for the FPP that we have issues with and will need to resolve at the next earliest time.

- Change Request Number: 08BON017

Date:  1/28/2009

Proposed by:  Rudd Turner

Location of Change:  BON section 2.2.2

Proposed Change:  Request you refer to the gas caps as 115%/120% TDG limits and not just 120%.

Reason for Change: For 2009 the Corps plans to continue use of the Camas/Washougal gauge to provide 115% TDG limits to set spill along with 120% TDG as measured at the Cascades Island gauge.

Comments from others:

Record of Final Action:

At this time we do not agree with the continued use of Camas/Washougal since it is not required by any of the water quality agencies and the use will limit the ability of the project spill water to safely pass migrants.

- Change Request Number:  08BON018 (As well as all the others similar ones)

Date: 1/6/09

Proposed by: CNWW-OD-T

Location: BON 5.4.3

Proposed Change:  Insert the following language.

5.4.3. Units may be operationally tested for up to 1 hour before going into maintenance status by running the unit at speed no load and various loads within the 1% criteria to allow pre-maintenance measurements and testing AND TO ALLOW ALL FISH TO MOVE THROUGH THE UNIT.  Units may be operationally tested after maintenance or repair while remaining in maintenance or forced outage status.  Operational testing may consist of running the unit for up to a cumulative time of 4 hours at speed no load and an additional cumulative period of 2 hours at full load (within 1% criteria) before it is returned to operational status.  Operational testing OF UNIT UNDER MAINTENANCE is in addition to a unit in run status (E.G. MINIMUM GENERATION) required for power plant reliability.  Operational testing may deviate from fish priority units and may require water that would otherwise be used for spill if the running unit for reliability is at its 1% minimum load.  Water will be used from the powerhouse allocation if possible, and water diverted from spill for operational testing will be minimized to that necessary to maintain and assure generation system reliability.

Reason for Change:  Allow unit operability testing and verification after maintenance activities.

Comments from others:

Record of Final Action:

Transport Appendix

We have concerns for all of these unit testing/maintenance turbine operation.  We are not aware of a situation where spill would need to be reduced to meet this need and if it was that operation needs to be scheduled well in advance to attempt to not impact the spill program, or be coordinated through the region forum.

Lastly we do not support the change of the language in the FPP under the Transport Section that modifies that start date of transport from May 1 to April 20.  We also believe the staggered start times should remain.