##### Construction

McNary:

- Turbine unit 1 taken out of service August 10 for annual maintenance.

- Turbine unit 2 taken out of service July 10 for 9-year overhaul.

- Turbine unit 5 taken out of service August 17 for annual maintenance.  Return to service will depend on when mobile crane service becomes available.

- Turbine unit 6 taken out of service August 19 for removal of water from the hub. The intake deck crane failed while removing a headgate from turbine unit 6.  The turbine unit’s return to service will depend when safe removal of crane from slot 6B is possible and when mobile crane service becomes available.

- Turbine units 7 & 8 remain out of service for transformer T4 replacement,

Ice Harbor:

- Turbine units 1 & 2 returned from service for annual maintenance and installation of lightning arrestors on bus bars.

- Trubine unit 3 taken out of service August 25 for annual maintenance.

- Turbine unit 4 remains out of service due to ripped VBS screen.

Lower Monumental:

- Turbine unit 6 returned to service from annual maintenance August 25.

Little Goose:

- Turbine unit 1 returned to service from annual maintenance on September 3.

- Turbine units 5 & 6 originally removed from service August 17 in support of Doble tests remained out of service due to a faulty electrical bushing until September 2

Lower Granite:

- Transformer line 2 outage limited turbine unit 2 generation until August 25 when the line returned to service.

- Turbine unit 6 taken out of service August 3 for annual maintenance.

Operations and Maintenance - Juvenile Fish Facilities

Collection for fish transport continues at Lower Granite, Little Goose and Lower Monumental and McNary dams.  All locations began fish truck operations on August 16.

McNary:

- North powerhouse loading remains in effect for temperature abatement in juvenile fishway.

Ice Harbor:

- Screen cleaner power supply failed August 4.  Repair parts have been ordered.  Powerhouse operators and fish facility personnel are the monitoring collection channel and inclined screen.

- A six inch by 2 foot rip found in VBS in slot 4A.  Slot dipped for fish and bulkheads set in place for repairs on August 20.  No fish recovered.  Repairs were completed August 24.

Lower Monumental:

- STSs switched from continuous to cycle mode on July 30 as average fork length of juvenile sockeye and Chinook are now greater than 120 mm.

Little Goose:

- The primary dewaterer weir motor failed July 20 and is currently undergoing repairs.  Water levels are being maintained by the opening and closure of orifices.

- Turbine unit 1 trash racks raked August 17 and 18.  Approximately 1 – 2 cubic yards of material removed.  A large log obstructs spans across all 3 trash racks.  A plan of action is being formulated for log removal.

Lower Granite:

- VBS inspections conducted August 21-23 revealed problems in slots 3A, 3B and 4B.   A bar was missing 3 bolts on the top VBS in slot 3A.  A large amount of debris was encountered 22 feet down on a VBS in slot 3B (possible tear).  Debris and a gap in the screen material were noted 29 feet down on the VBS in slot 4B.

Operations and Maintenance - Adult Fish Facilities

McNary:

- Oregon Ladder: North AWS taken out of service May 28 following failure.  South AWS continues to provide sufficient water.  South AWS trash rack raked August18 with the help of divers.  Divers discovered at least one broken basket and separated carrier chain at the north AWS.  Since repairs will require an extended outage and a large floating crane, this work has been deferred until the next winter maintenance period.  In the meantime, the south AWS is providing sufficient water to meet fish passage needs through the gravity-fed conduit.

- Fish Pumps: Pumps #1, #2 & #3 are in service.  Potable water supply problems are causing interruptions in service as domestic water is used to cool pump bearings.  Maintenance personnel are still working to isolate and resolve the supply problems.

Ice Harbor:

- North Shore Fish Pumps: Fish pumps #1 & #2 in service.  Fish Pump #3 on standby.

- North Shore Channel: Sonar based channel elevation measuring equipment failed July 28.  Older meta-tape measuring system placed into service.  Repair parts have been ordered.

Lower Monumental:

- Fish Pumps 1 & 2 in service.  Fish Pump #3 remains out of service for diffuser assembly repairs and bearing housing replacement.

Little Goose:

- NPE3: The bulkhead sealing off this entrance is cracked and water is flowing into the spill basin.  NSE-2 weir depth has been raised to 2.5 feet to maintain channel - tailwater differentials at the north shore.  Otherwise, fishway performance does not appear to be adversely affected at this time and adult fish are successfully passing the count window.  Repairs will likely take place during the winter maintenance season.

- Adult collection channel: A two foot section of the fallout fence has separated from the support frame.  Adult fish appear to be passing though this area safely.

Lower Granite:

- Fish pumps 1 and 3 in operation.  Fish pump 2 repairs completed July 10 and placed in standby status until planned tests can be completed.

Other

Spill Ended at all locations on August 31.

McNary:

- Juvenile lamprey research ended with the close of barge operations.  Adults lamprey study still in progress.

Ice Harbor:

- RSW in operation.

- Cooling water strainers in turbine units 1, 2 and 4 were inspected August 17.  One juvenile lamprey mortality was recovered from the turbine unit 1 strainers and an unidentifiable mortality was found in the turbine unit 4 strainers.

- Turbine unit 3 cooling water strainer checked August 25 – no fish found.

Lower Monumental:

- Cooling water strainers inspected August 19, no fish found.

Little Goose:

- Cooling water strainers were inspected in turbine units 1,2,4,5 and 6 on August 10.  No fish were found.

Lower Granite:

- Adult trap operation suspended July 19 due to high water temperatures and problems with the slide gate air valve control to the anesthetic tank.  Trap operations resumed August 18.

- Cooling water strainers inspected in turbine unit 4 on July 14.  One live and 3 dead juvenile lamprey were recovered.