## Sheet2
Transmission Outages that have potential impacts to Fish operations
Equipment Outage | Date(s) | Hours | Impacted Generation | Notes
September-10 (45 day outage planning process completed)
John Day PH-John Day 4 500kV line | 2010-09-02 | 1000-1200 | Forces out units 13-16 | PH relay trip checks
October-10 (tentative, 45 day outage planning process not completed)
North Bonneville-Ross 1 230kV line | 10/18/10-10/22/10 | Continuous | Bonneville 230kV generation limited to 400 MW | Replace analog transfer trip with digital equipment
Dworshak PH-Dworshak 1 500kV line | 10/20/10-10/24/10 | Continuous | Forces out units 2 & 3 | Spacer damper replacement
November-10 (tentative, 45 day outage planning process not completed)
Little Goose PH-Little Goose 1 500kV line | 11/29/10-12/10/10 | Continuous | Forces out all units | Replace line CVTs at Little Goose substation
Future Outages (Tentative)
Little Goose PH-Little Goose 1 500kV line | Fall 2011 | 2 days | Forces out units 1-6 | Spacer damper replacement
Lower Granite PH-Lower Granite 1 500kV line | Fall 2011 | 2 days | Forces out units 1-6 | Spacer damper replacement
McNary PH-McNary 1-4 230kV lines | 14 days, August 2011 | Daily | Forces out units 1-8 | Stringing conductor for new McNary-John Day 500kV line over powerhouse lines
McNary PH-McNary 5 230kV line and McNary PH-McNary 6 115kV line | 14 days, August 2011 | Daily | Forces out units 9-14 | Stringing conductor for new McNary-John Day 500kV line over powerhouse lines

## Sheet1
Transmission Outages that have potential to limit generation
Equipment Outage | Date(s) | Hours | Impacted Generation | Notes
September-10 (45 day outage planning process completed)
Detroit PH 2 230kV line | 8/30/10-9/16/10 | Continuous | Forces out unit 2 | PH work
Dworshak-Taft 1 500kV line | 8/31/10-9/3/10 | Continuous | Unit 1 required to generate to support 115kV transmission system | XJ-7 opened during Dworshak-Taft 1 500kV line outage to prevent through flow of power to 115kV transmission system
John Day PH-John Day 4 500kV line | 2010-09-02 | 1000-1200 | Forces out units 13-16 | PH relay trip checks
Libby PH-Libby 2 230kV line | 2010-09-07 | 0630-1700 | Forces out Libby units 3-5. Unit 5 will be available after 1200. Units 3-4 will be O/S unit 10/7/10. | PH work for transformer T2 transverse bus isolation
Columbia Falls-Flathead 1 230kV line | 2010-09-13 | 0400-2300 | 50 MW minimum and 150 MW max gen level at Hungry Horse. Libby PH 1 (units 1 & 2) gen limited to 160 MW. Combined Libby and Hungry Horse gen limited to 680 MW. | Install new strain bus and move overhead ground wire at Flathead substation to accommodate new point of delivery for Flathead Electric Co-op.
Lower Monumental-Ashe 1 500kV line | 9/13/10-9/20/10 | Continuous | Combined output of Lower Monumental, Little Goose and Lower Granite limited to 1700 MW. | Replacing line CVT's at Lower Monumental
Noxon-Libby 1 230kV line | 9/14/10-9/17/10 | Continuous | Libby gen limited to 350 MW. Combined Libby and Hungry Horse gen limited to 600 MW. | Line insulator and hardware work
Blue River tap to Cougar-Thurston 1 115kV line | 2010-09-26 | 0001-0800 | Forces out Cougar gen | Replace pole `
October-10 (tentative, 45 day outage planning process not completed)
Libby PH-Libby 2 230kV line | 2010-10-07 | 0700-1300 | Forces out Libby unit 5. Units 3 & 4 already O/S. | Install jumpers to reconnect transformer T2
Chief Joseph PH-Chief Joseph 6 500kV line | 10/18/10-10/22/10 | Continuous | Forces out units 21-27 | Replace line CVT's
North Bonneville-Ross 1 230kV line | 10/18/10-10/22/10 | Continuous | Bonneville 230kV generation limited to 400 MW | Replace analog transfer trip with digital equipment
Dworshak PH-Dworshak 1 500kV line | 10/20/10-10/24/10 | Continuous | Forces out units 2 & 3 | Spacer damper replacement
November-10 (tentative, 45 day outage planning process not completed)
Little Goose PH-Little Goose 1 500kV line | 11/29/10-12/10/10 | Continuous | Forces out all units | Replace line CVTs at Little Goose substation
Future Outages (Tentative)
Little Goose PH-Little Goose 1 500kV line | Fall 2011 | 2 days | Forces out units 1-6 | Spacer damper replacement
Lower Granite PH-Lower Granite 1 500kV line | Fall 2011 | 2 days | Forces out units 1-6 | Spacer damper replacement
Chief Joseph PH-Chief Joseph 5 500kV line | Fall 2011 | 2 days | Forces out units 17-20 | Spacer damper replacement
Chief Joseph PH-Chief Joseph 6 500kV line | Fall 2011 | 2 days | Forces out units 21-27 | Spacer damper replacement
McNary PH-McNary 1-4 230kV lines | 14 days, August 2011 | Daily | Forces out units 1-8 | Stringing conductor for new McNary-John Day 500kV line over powerhouse lines
McNary PH-McNary 5 230kV line and McNary PH-McNary 6 115kV line | 14 days, August 2011 | Daily | Forces out units 9-14 | Stringing conductor for new McNary-John Day 500kV line over powerhouse lines
Outages that are 1 hour or less are not shown
RED are changes since last update |  |  |  | mrv 8/26/10
OFFICIAL USE ONLY
May be exempt from public release under the Freedom of Information Act (5 U.S.C. 552), exemption number and category:
Exemption 2 - Circumvention of Statute
BPA review required before public release.
Name/Org: Mike Viles - BPA Date: 8/26/10