## Sheet1
CRITERIA (Unsat Performance): Life Safety/Economic Impacts/ENS Impact/Legal/Warning Time/Scale of Disruption
FOCUS AREAS LEGEND: Cranes/Fish Facilities/Gates/General/Hydrologic/Jetties/Levees/Pile Dikes/Readiness/Seismic/Stilling Basins/Env Protection (oil spill)
Focus Area | House Delegation | Business Line | FY12 Budget NWP ID/Rank For NWD | NWD RANK | District Rank | Project | Asset(s) Description | Feature Code | RPUID | Phase | Description of Unsatisfactory Performance | Frequency | Condition | Consequences | Probability | Consequences of the Unsatisfactory Performance |  |  | Relative Risk | Relative Risk Category | PM or POC | Work Type: Study/ Repairs | $ Source | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | District Strategy | Comments | Contingency Operations Item (Yes/No/ Maybe) | Contingency Operations Description
Fish Facilities | [5 empty] | BON | BI Fish valves (FV4-3, 4-4) | [5 empty] | F | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Auxilliary water supply conduit (AWS) | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Diffusers | [5 empty] | F | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | OR-4 | ENS | NWP-25 |  |  | Lookout Point/Dexter | Willamette Hatchery Water Well | 05 |  | Study / P&S | Spring 2007, well capacity continues to decline causing cavitation/supersaturation resulting in loss of 600,000 rainbow trout fry. ODFW saving extra eggs at other facilities. Overtap of acquifer by others causing shortage of well capacity. | Constant |  | Very High | Very Likely | Moderate - risk of fish kill in hatchery. Not meet Corps mitigation responsibility, possible litigation. | 6 | 7 | 2.4 | 2 | Simmons | Study | O&M | 2010: 125; 2011: 0; 2012: TBD | Serious issue, but "moderate" effect lowers matrix rank to "6". | May install disinfection system on existing water well
Fish Facilities | WA-3 | FRM |  |  |  | MSH Sediment Retention Structure | Spillway | 04 |  | Study / P&S | Volitional upstream migration to about 50 miles if anadromous fish habitat blocked by spillway obstructions. Fish currently trucked upstream. | Constant |  | Very High | Very Likely | Moderate - Impacts to listed species (Toutle Ri). Trucked fish release pts provide unknown survival. 2006 steelhead fish kill from sediment at collection fac | 6 | 8 | 2.5 | 2 | Kuhn | Study/P&S | CG | 2008: 1500; 2009: 0; 2010: 10600; 2011: 17700; 2012: TBD | Possible authority issues | 08: P&S + contract (likely rock removal) 09: Complete contract
Fish Facilities | [5 empty] | BON | CI Auxilliary water supply conduit (AWS) | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | OR-4 | ENS |  |  |  | Willamette Valley (LOP/DEX (51% funding) + 11 other WV projects) | Leaburg Hatchery | 05 |  | Rpt/Rehab | ESA noncompliance, disease (IHNV) problems | Nearly Constant |  | Moderate | Likely | Moderate | 9 | 9 | 2.6 | 2 | Simmons | Study | MMR or O&M | 2009: 150; 2010: 550; 2011: 275; 2012: TBD |  | Start design of hatchery replcmt. Replace or re-build fish hatchery w/ comparable facility. Corps owns-May be shut down. $24M
Fish Facilities | OR-4 | ENS |  |  |  | Detroit/Big Cliff (Marion Forks Fish Hatchery) | Screen Intakes |  |  | Study / P&S | Need new screen intakes | Nearly Constant |  | Moderate | Likely | Low | 14 | 15 | 3.5 | 3 | Bardy |  |  | 2011: 464; 2012: TBD |  | Estimate is $1M (New item in FY11 budget)
Fish Facilities | OR-4 | ENS |  |  |  | Lookout Point/Dexter (Willamette Hatchery) | Screen Intakes |  |  | Study / P&S | Need new screen intakes | Nearly Constant |  | Moderate | Likely | Low | 14 | 15 | 3.5 | 3 | Smith |  |  | 2011: 515; 2012: TBD |  | Estimate is $1M (New item in FY11 budget)
Fish Facilities | [5 empty] | BON | CI Diffusers | [5 empty] | F | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Fish exit bulkhead | [5 empty] | F | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Auxilliary water supply conduit (AWS) | [5 empty] | F | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Diffusers | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | PH1 ITS endgate | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | spill gates | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | spill hoists | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
Fish Facilities | [5 empty] | BON | spillway gantry cranes | [5 empty] | D | I |  |  |  |  | 1 |  | Hausmann
HATCHERIES | [5 empty] | McKenzie | Emergency Power Backup - Incubation Bldg | [5 empty] | N/A | I - High |  |  |  |  | 1.1 |  | Klatte |  |  | 2011: 40000 |  | Need backup power for critical water supply strainers
HATCHERIES | [5 empty] | Bonneville | Well Enunciation – for hatchery wells | [5 empty] | F-Failed | II - Medium-High |  |  |  |  | 1.2 |  | Klatte |  |  | 2011: 25000 |  | No longer have well enunciation at hatchery -requested by COE project
Fish Facilities |  | ENS |  |  |  | JDA | JDS- AWS Turbine #3 |  |  | Overhaul | # 3 OOS now, current overhaul started in 2008 |  | F- failed | II- medium -high |  | High Risk |  |  | 1.3 |  | Zyndol | Repairs | CG | 2011: $750K |  | # 3 OOS now, current overhaul started in 2008
Fish Facilities |  | ENS |  |  |  | JDA | JD STS camera device |  |  | Repair/ Replacement | Failed |  | F- failed | II- medium -high |  | High Risk |  |  | 1.3 |  | Zyndol | Repairs | O&M | [10 empty] | Failed in Aug. '10, new video parts ordered. ETR May '11
Fish Facilities |  | ENS |  |  |  | JDA | JDN AWS pump gantry crane |  |  | Repair | Failed |  | F- failed | II- medium -high |  | High Risk |  |  | 1.3 |  | Zyndol | Repairs | O&M | [10 empty] | Gear box failed. Estimated cost to repair - $ 70 K
Fish Facilities |  | HYDRO |  |  |  | JDA | Spillway- control for TSW s |  |  | Modification | Failed |  | F -failed | II- medium -high |  | High Risk |  |  | 1.3 |  | Zyndol | Repairs | CG | [10 empty] | Needs modification to bay 18 & 19 control system
HATCHERIES | [5 empty] | McKenzie | Emergency Power Backup - Intake | [5 empty] | C - Marginal | I - High |  |  |  |  | 1.3 |  | Klatte |  |  | 2011: 40000 |  | Replace 1979 portable generator with full system generator
HATCHERIES | [5 empty] | McKenzie | Secondary Water Supply for Rearing Ponds | [5 empty] | D - Poor | I - High |  |  |  |  | 1.3 |  | Klatte |  |  | 2011: 1500000 |  | Water supply is interrupted by EWEB operations
Fish Facilities | [5 empty] | BON | WS Entrance gates | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Program Logic Controller (SA-24 board) | [5 empty] | D | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | PH1 ITS channel | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | B2CC bulkhead | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | B2CC channel | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | STSs | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | DSM2 orifices | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | DSM2 airburst system | [5 empty] | B | III |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | DSM2 mechanical screen cleaners | [5 empty] | D | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | JMF transport pipe | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | Juvenile monitoring facility | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Fish exit bulkhead | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Fish valve trashracks | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Fish valves (FV3-7, 3-9, 1-1) | [5 empty] | C | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Serpentine weirs | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Overflow weirs | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Fixed entrance weir | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Program Logic Controller | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Fish exit bulkhead | [5 empty] | C | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Fish valve trashracks | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Fish valves (FV5-9, 5-3, 5-4) | [5 empty] | C | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Serpentine weirs | [5 empty] | C | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Overflow weirs | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Program Logic Controller | [5 empty] | C | II |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Serpentine weirs | [5 empty] | B | I |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Diffuser grating | [5 empty] | F | III |  |  |  |  | 2 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS SA-24 board | [5 empty] | F | III |  |  |  |  | 2 |  | Hausmann
Fish Facilities | OR-2 WA-4 | ENS |  |  |  | TDA | Auxiliary Water Supply Backup |  |  | Repair | Dependence on single source of fish attraction water |  |  |  |  | Unable to pass fish through east fish ladder |  |  | 2.2 | 2 | Twiner | Repairs | O&M | 2010: 103; 2012: TBD |  | Plan is to use old fish lock to provide emergency auxiliary water, FY10 funding secured for work; FY11 funding required for testing. | Yes | Spill gates 12, 14-23 were greased. Bays 10, 11 and 13 are restricted due to wire rope issues. Bays 16, 18 and 19 are restricted due to concerns over structural deformation. Bay 23 is restricted due to undercutting of the apron.
HATCHERIES | [5 empty] | McKenzie | Rearing Ponds Resurface / Wall Coatings | [5 empty] | D - Fair | III - Medium |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 250000 |  | Resurface and seal worn surfaces in rearing ponds
HATCHERIES | [5 empty] | McKenzie | Replace Water Chiller in Incubation System | [5 empty] | D - Poor | II - Medium - High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 45000 |  | Existing chiller does not run properly without extensive repairs
HATCHERIES | [5 empty] | Bonneville | Intake structure (21' x 48.6' x 8.5' concrete) | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 1500000 |  | Existing river intake structure does not meet NOAA requirements
HATCHERIES | [5 empty] | Bonneville | Old Public Restroom and septic system (18'8" x 14') | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 95000 |  | Provide ADA compliant public facilities for 500k tourist per year
HATCHERIES | [5 empty] | Bonneville | Roadways (asphalt ) | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 70000 |  | Resurface 35,000 sq. ft. of asphalt in very poor condition
HATCHERIES | [5 empty] | Bonneville | Hatchery water system/valves, battery C&D | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 80000 |  | Underground valves continue to fail, 20 valves need replacing
HATCHERIES | [5 empty] | Cole M Rivers | Pond Safety Railings | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 250000 |  | Current OSHA requirement
HATCHERIES | [5 empty] | Cole M Rivers | Concrete joint repair | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 50000 |  | Replace sealant in pond expansion joints and cracks
HATCHERIES | [5 empty] | Cole M Rivers | Fish feeding system | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 450000 |  | Replace original mechanized fish feeding system
HATCHERIES | [5 empty] | Cole M Rivers | Pollution Abatement Pond sealing | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 10000 |  | Clean and seal asphalt pond liner
HATCHERIES | [5 empty] | Cole M Rivers | Hatchery building fire detection and alarm systems | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 10000 |  | Repair and upgrade fire detection and alarm systems
HATCHERIES | [5 empty] | Cole M Rivers | Rearing pond concrete resurfacing | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 500000 |  | Resurface and seal worn surfaces in fish ponds
HATCHERIES | [5 empty] | McKenzie | Inspection / Upgrade Incubation Strainers | [5 empty] | B - Fair | II - Medium - High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 50000 |  | 1975 incubation water supply strainers / possible parts renewed
HATCHERIES | [5 empty] | Leaburg | Pond safety railings | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 200000 |  | Current OSHA requirement
HATCHERIES | [5 empty] | Leaburg | Intake structure screening compliance | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 2000000 |  | Existing river intake structure does not meet NOAA requirements
HATCHERIES | [5 empty] | Leaburg | Supply water disinfection system | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 2500000 |  | Improve hatchery water quality and disease prevention
HATCHERIES | [5 empty] | Leaburg | Replace earthen supply channel | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 300000 |  | Prevent erosion of banks and water loss through leakage
HATCHERIES | [5 empty] | Leaburg | Repair access to fish viewing platform | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 20000 |  | Construct ADA compliant public access
HATCHERIES | [5 empty] | Leaburg | Construct predator exclusion structure | [5 empty] | D-poor | II - Medium-High |  |  |  |  | 2.2 |  | Klatte |  |  | 2011: 300000 |  | Prevent predation to minimize loss and disease transmittance
Fish Facilities | OR-2 WA-4 | ENS | NWP-20 |  |  | JDA | Bonneville Hatchery Well Field | 05 |  | Study | Hatchery well field has iron bacteria problem | Nearly Constant |  | Moderate | Likely | Critical - loss of fish production, failure to meet contractual obligations | 5 | 6 | 2.3 | 2 | Klatte | P&S/Repair | O&M | 2008: 125; 2010: 0; 2011: 0; 2012: TBD |  | Temperature increasing, iron bacteria. Need budget for P&S/Repair
Fish Facilities |  | ENS |  |  |  | JDA | JD STS crane |  |  | Overhaul | Failure risk high |  | D-poor | II- medium -high |  | Medium Risk |  |  | 2.3 |  | Zyndol | Study/P&S | CG | 2010: 0; 2011: 0 |  | Needs crane / control system overhaul (est. at $ 1.5 million)
Fish Facilities |  | ENS |  |  |  | JDA | JDSouth Automation |  |  | Replacement | unsatisfactory compliance |  | D-poor | II- medium -high |  | Medium Risk |  |  | 2.3 |  | Zyndol | Repairs | O&M | 2011: $6K |  | New automation to be completed before 1 March '11.
Fish Facilities |  | ENS |  |  |  | JDA | Bird predators hazing |  |  | Fish Protection | High fish mortality |  | B-fair | II- medium -high |  | Medium Risk |  |  | 2.3 |  | Zyndol |  | O&M | 2011: $180K |  | Boat hazing, 2 shifts cost is $ 180 K for FY ' 11.
Fish Facilities |  | ENS |  |  |  | JDA | JDN- Bulkhead (Galleon) crane D- poor |  |  | Replacement | Unable to provide maintenance support |  | D-poor | II- medium -high |  | Medium Risk |  |  | 2.3 |  | Zyndol | Repairs | CG | [10 empty] | Need funding for 15 ton crane
Fish Facilities |  | HYDRO |  |  |  | JDA | Main unit trashracks |  |  | Repair | Unable to rake damaged trash racks |  | D-poor | II- medium -high |  | Medium Risk |  |  | 2.3 |  | Zyndol | Study | MMR or O&M | [10 empty] | Some can't be raked, need to assess damage
Fish Facilities | OR-3 WA-3 | ENS | NWP-24 |  |  | BON | Fish Ladders, B-Branch & Cascade Is. | 05 |  | Study / P&S | diffuser structural problems and air entrainment by fish valves that causes gas supersaturation of fishway | Nearly Constant |  | High | Very Likely | Moderate | 6 | 7 | 2.4 | 2 | Smith |  |  | 2010: 100; 2011: 0; 2012: 16000 |  | Per Bonn Project personnel: "it was decided to leave this item on the CI list but not budget in FY11. Have ARRA funds for Fishway Diffuser Valves - ARRA P&S ($319k) will have impact on determining what to do for this effort. Est. of $1.6M for repair. Without fishways, only adult passage in WA side.
Fish Facilities |  | ENS |  |  |  | JDA | JD STSs |  |  | Overhaul | Main Unit can't run w/ out STS |  | C- marginal | II- medium -high |  | Medium Risk |  |  | 2.4 |  | Zyndol | Study/P&S | CG | [10 empty] | Overdue for overhaul since approx. 2000
Fish Facilities |  | ENS |  |  |  | JDA | JD North AWS Fish Pumps |  |  | Improvement | Poor adult attraction |  | C- marginal | II- medium -high |  | Medium Risk |  |  | 2.4 |  | Zyndol | Repairs | CG | [10 empty] | Replacement with new pumps planned for FY '12 (CRFM)
Fish Facilities |  | ENS |  |  |  | JDA | Zebra Mussel Prep |  |  | Study | Negative effect on fish passage |  | C- marginal | II- medium -high |  | Medium Risk |  |  | 2.4 |  | Zyndol | Study | CG | [10 empty] | Need contingency plan
Fish Facilities |  | NAVIGATION |  |  |  | JDA | Spillway- trunion lubrication C-marginal |  |  | Repair | Inability to transport barged fish |  | C-marginal | II- medium -high |  | Medium Risk |  |  | 2.4 |  | Zyndol | P&S/Repair | [11 empty] | Increased usage for fish passage requires automatic lube
Fish Facilities |  | HYDRO |  |  |  | JDA | Navigation Lock |  |  | Improvement | Spillway gate failure |  | M-marginal | I-high |  | Medium Risk |  |  | 2.4 |  | Zyndol | Study | CG | [10 empty] | Navlock failure results in no fish barge transport
Fish Facilities | OR-2 WA-4 | ENS /Hydro |  |  |  | JDA | Submerged Traveling Screen Rehab | 05 |  | Study / P&S | STS needs major overhaul. Work w/ JDA sandblast/paint faciity. STS failure causes unit shutdown. | Nearly Constant |  | Moderate | Likely | Moderate | 9 | 8 | 2.5 | 2 | Smith |  |  | 2007: 200 (UFR); 2012: TBD |  | 200k for P&S on sand blast bldg for in-house forces to rehab STS screens.
HATCHERIES | [5 empty] | McKenzie | Inspection / Upgrade of main intake | [5 empty] | C - Marginal | II - Medium - High |  |  |  |  | 2.5 |  | Klatte |  |  | 2011: ? $150000 |  | Inspection of 1975 intake structure with possible parts replaced
HATCHERIES | [5 empty] | McKenzie | Adult Holding Ponds Resurfacing / Wall Coatings | [5 empty] | B - Fair | II - Medium - High |  |  |  |  | 2.5 |  | Klatte |  |  | 2011: 60000 |  | Resurface and seal worn surfaces in holding ponds
HATCHERIES | [5 empty] | McKenzie | Expand Pollution Abatement Pond | [5 empty] | C - Marginal | II - Medium - High |  |  |  |  | 2.5 |  | Klatte | [12 empty] | DEQ regulations may warrant expansion | bar: 2011
HATCHERIES | [5 empty] | McKenzie | Add Bio Swale Filtering System for Treated Water | [5 empty] | N/A | II - Medium - High |  |  |  |  | 2.5 |  | Klatte | [12 empty] | To comply with DEQ regulations for chemical use / possible | bar: 2011
HATCHERIES | [5 empty] | McKenzie | Adult Pond Treatment Pump | [5 empty] | B - Fair | II - Medium - High |  |  |  |  | 2.5 |  | Klatte |  |  | 2011: 10000 |  | Repalce existing pump
HATCHERIES | [5 empty] | Leaburg | Update supply water flow measurement system | [5 empty] | C- marginal | II - Medium-High |  |  |  |  | 2.5 |  | Klatte |  |  | 2011: 25000 |  | Update flow measuring system in supply channel
HATCHERIES | [5 empty] | Leaburg | Concrete joint repair in rearing ponds | [5 empty] | C- marginal | II - Medium-High |  |  |  |  | 2.5 |  | Klatte |  |  | 2011: 150000 |  | Replace sealant in pond expansion joints and cracks
HATCHERIES | [5 empty] | Cole M Rivers | Lead-based paint assessment, abatement plan | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 25000 |  | Comprehensive lead paint assessment and management plan
HATCHERIES | [5 empty] | Cole M Rivers | Asbestos assessment and abatement plan | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 25000 |  | Comprehensive ACM assessment and management plan
HATCHERIES | [5 empty] | Cole M Rivers | Intake structure floating weed barrier | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 25000 |  | Replace existing barrier
HATCHERIES | [5 empty] | Cole M Rivers | Convert old incubation filter beds for early rearing | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 50000 |  | Increase early rearing capacity
HATCHERIES | [5 empty] | Cole M Rivers | Smolt release channel | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 2000000 |  | Construct open channel for on-site smolt releases
HATCHERIES | [5 empty] | Cole M Rivers | Angler universal access | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 1500000 |  | Constuct ADA compliant public access
HATCHERIES | [5 empty] | Leaburg | Residence basement repairs | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 70000 |  | Prevent water infiltration in residence basements
HATCHERIES | [5 empty] | Leaburg | Replace fish feeding system | [5 empty] | D-poor | III - Medium |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 300000 |  | Replace original mechanized fish feeding system
HATCHERIES | [5 empty] | McKenzie | Pond Safety Railings | [5 empty] | C - Marginal | II - Medium - High |  |  |  |  | 2.6 |  | Klatte |  |  | 2011: 125000 |  | Current OSHA requirement
Fish Facilities | [5 empty] | BON | PH1 ITS manual chain gates | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | PH1 ITS PLC | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | VBSs | [5 empty] | B | II |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | DSM2 dewatering screen | [5 empty] | B | II |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | spillway PLC | [5 empty] | B | II |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Fish count crowder | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Diffuser grating | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Fish count crowder | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Diffuser grating | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Entrance gates, adjustable | [5 empty] | D | IV |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Fish valve (FV6-9) | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Fish count crowder | [5 empty] | C | III |  |  |  |  | 3 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Overflow weirs | [5 empty] | B | II |  |  |  |  | 3 |  | Hausmann
Fish Facilities |  | ENS |  |  |  | JDA | JDS -AWS Turbines # 1 & 2 |  |  | Overhaul | AWS failure/ unable to meet passage criteria |  | B - fair | II- medium -high |  | Moderate Risk |  |  | 3.2 |  | Zyndol | Repairs | CG | [10 empty] | Overdue for overhaul
Fish Facilities |  | ENS |  |  |  | JDA | Avian lines over tailrace BRZ |  |  | Repair | High avian predation |  | B-fair | II- medium -high |  | Moderate Risk |  |  | 3.2 |  | Zyndol |  | O&M | [10 empty] | New in 2010. Will require annual maintenance /repairs
Fish Facilities |  | ENS |  |  |  | JDA | SMF-PDS ,separator, valves, gates |  |  | Repair | Unsatisfactory fish monitoring |  | B-fair | II- medium -high |  | Moderate Risk |  |  | 3.2 |  | Zyndol | Repairs | O&M | [10 empty] | SMF is over 12 yo., could require increased maintenance soon
HATCHERIES | [5 empty] | Bonneville | 1977 International 3 ton truck (Boom truck) | [5 empty] | D-poor | IV - Low |  |  |  |  | 3.2 |  | Klatte |  |  | 2011: 70000 |  | Boom truck is 34 years old
HATCHERIES | [5 empty] | Bonneville | Cushman Haulster with white fiberglass cab (gas) blk rack | [5 empty] | D-poor | IV - Low |  |  |  |  | 3.2 |  | Klatte |  |  | 2011: 19000 |  | Engine past useful life had to get parts for
HATCHERIES | [5 empty] | Cole M Rivers | Equipment and material storage | [5 empty] | D-poor | IV - Low |  |  |  |  | 3.2 |  | Klatte |  |  | 2011: 200000 |  | Additional secure storage
HATCHERIES | [5 empty] | Cole M Rivers | Office building HVAC upgrade | [5 empty] | D-poor | IV - Low |  |  |  |  | 3.2 |  | Klatte |  |  | 2011: 50000 |  | Replace, upgrade 40 year old heating, AC system
HATCHERIES | [5 empty] | Leaburg | Entrance road drainage system | [5 empty] | D-poor | IV - Low |  |  |  |  | 3.2 |  | Klatte |  |  | 2011: 75000 |  | Install drainage system on entrance road
Fish Facilities |  | ENS |  |  |  | JDA | Fishladder Expansion Joints |  |  | Repair | Could lead to structual instability |  | C- marginal | III-medium |  | Moderate Risk |  |  | 3.3 |  | Zyndol | Repairs | O&M | 2011: $27K |  | Searching for improved material/methods to seal leaks
Fish Facilities |  | ENS |  |  |  | JDA | SMF -AWS supply pipes |  |  | Prevention/ Maintenance | Pipe corrosion |  | C- marginal | III-medium |  | Moderate Risk |  |  | 3.3 |  | Zyndol | Repairs | O&M | [10 empty] | Needs corrosion / new paint protection
HATCHERIES | [5 empty] | Bonneville | Raceway (Battery A) (22 ponds) | [5 empty] | C-marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 90000 |  | Resurface bottom of 9 ponds to extend life of ponds
HATCHERIES | [5 empty] | Bonneville | Display trout pond (lower) | [5 empty] | C-marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte | [12 empty] | Currently working on this asset
HATCHERIES | [5 empty] | Bonneville | Sturgeon Pond | [5 empty] | C-marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Garon fish feeder 2L100-6Hsw (x28) | [5 empty] | C-marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 120000 |  | Feeder are 34 years old, and parts are no longer available
HATCHERIES | [5 empty] | Bonneville | Display trout pond (upper) | [5 empty] | C-marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte | [12 empty] | Currently working on this asset
HATCHERIES | [5 empty] | Cole M Rivers | Incubation water filtration & sterilization | [5 empty] | C- marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 100000 |  | Improve water quality and disease prevention
HATCHERIES | [5 empty] | Cole M Rivers | Emergency power system modification | [5 empty] | C- marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 30000 |  | Provide backup power to additional electrical loads
HATCHERIES | [5 empty] | Leaburg | Intake structure floating debris barrier | [5 empty] | C- marginal | III - Medium |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 25000 |  | Repair or replace existing intake structure debris boom
HATCHERIES | [5 empty] | McKenzie | Main Intake Compliance | [5 empty] | B - Fair | II - Medium - High |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 700000 |  | Existing intake structure does not meet NOAA requirements
HATCHERIES | [5 empty] | McKenzie | Cogswell Creek Intake Compliance/Passage | [5 empty] | B - Fair | III - Medium |  |  |  |  | 3.3 |  | Klatte |  |  | 2011: 600000 |  | Existing intake structure does not meet NOAA requirements
HATCHERIES | [5 empty] | Bonneville | Hatchery water system/ valves/manholes | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Spawning room, administrative offices, visitor's center, public restrooms (New roof 2010) | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 100000 |  | Outdated visitor center, public restrooms and heating system
HATCHERIES | [5 empty] | Bonneville | Maintenance building | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 150000 |  | Building needs new roof (high priority maintenance need)
HATCHERIES | [5 empty] | Bonneville | Pond pollution abatement (3,000 sq. feet) | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Power fish crowder with rails (sweep 8' x 12') | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte | [12 empty] | Critical asset in fair condition - needs parts & routine maintenance
HATCHERIES | [5 empty] | Bonneville | Caterpillar forklift (gas) Older 4000 lb cap. | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine professional maint.
HATCHERIES | [5 empty] | Cole M Rivers | Hatchery monitoring and alarm system | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 30000 |  | Update existing alarm system
HATCHERIES | [5 empty] | Cole M Rivers | Intake structure screening compliance | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 5000000 |  | Existing river intake structure does not meet NOAA requirements
HATCHERIES | [5 empty] | Leaburg | Hatchery monitoring and alarm system | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 30000 |  | Update existing alarm system
HATCHERIES | [5 empty] | Leaburg | Rearing pond concrete resurfacing | [5 empty] | B-fair | II - Medium-High |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 400000 |  | Repair and resurface existing rearing pond concrete surface
HATCHERIES | [5 empty] | McKenzie | Equipment and Material Storage | [5 empty] | D - Poor | IV - Low |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 35000 |  | Additional secure storage
HATCHERIES | [5 empty] | McKenzie | New Domestic Well | [5 empty] | C - Marginal | IV - Low |  |  |  |  | 3.4 |  | Klatte |  |  | 2011: 50000 |  | Add well to increase water availability
HATCHERIES | [5 empty] | Bonneville | Auxiliary water line to ponds | [5 empty] | A-good | I - High |  |  |  |  | 3.5 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Domestic water system/five hydrants | [5 empty] | A-good | I - High |  |  |  |  | 3.5 |  | Klatte | [12 empty] | Critical asset in good condition
Fish Facilities | [5 empty] | BON | WS Floating orifice gates (FOGs) | [5 empty] | D | V |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS FOG bulkheads/transverse bulkheads | [5 empty] | B | III |  |  |  |  | 4 |  | Hausmann
Fish Facilities | ENS |  |  | John Day |  | BON | PH1 ITS automated chain gates | Moderate Risk | 3.3 |  |  |  | B | III |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | TIES | [5 empty] | C | V |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | PH2 trashracks | [5 empty] | C | IV |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Log booms | [5 empty] | D | V |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Fish exit trashrack | [5 empty] | C | V |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Lamprey passage structure (LPS) | [5 empty] | B | III |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Picket leads | [5 empty] | C | IV |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Entrance gate, adjustable | [5 empty] | C | IV |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Fish exit trashrack | [5 empty] | C | V |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Picket leads | [5 empty] | C | IV |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Fixed entrance weir | [5 empty] | A | II |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Log booms | [5 empty] | C | V |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Fish valve trashrack | [5 empty] | B | IV |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Lamprey passage structure (LPS) | [5 empty] | A | III |  |  |  |  | 4 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Picket leads | [5 empty] | B | IV |  |  |  |  | 4 |  | Hausmann
HATCHERIES | [5 empty] | Bonneville | Caterpillar forklift (gas) Newer 5000 lb cap. | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs routine professional maint.
HATCHERIES | [5 empty] | Bonneville | Screens (perf. Alum. Alloy) | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Submersible maintenance water well pump 15 hp 460V | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Coffelt fiberglass tank for electroshocker | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | International 16' flatbed with 15 ton hoist (Lib Truck) | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs parts & routine maintenance
HATCHERIES | [5 empty] | Bonneville | Saylor Beall air compressor | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | GMC 1 ton van (Feed Van) | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs routine professional maint.
HATCHERIES | [5 empty] | Bonneville | Diesel/gasoline 1100 gal above ground | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Electroanesthesia machine | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition
HATCHERIES | [5 empty] | Bonneville | Pneumatic stunner (broodstock) | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs parts & routine maintenance
HATCHERIES | [5 empty] | Bonneville | Pneumatic stunner (broodstock) | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs parts & routine maintenance
HATCHERIES | [5 empty] | Bonneville | Fish ID Detector w/gate | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Fish tag detector, handheld wand | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Jensorter w/table (fish egg sorter) (x2) 2010 | [5 empty] | A-good | II - Medium-High |  |  |  |  | 4.1 |  | Klatte | [12 empty] | Critical asset in good condition
Fish Facilities |  | BPA |  |  |  | JDA | Pikeminnow dam angling |  |  | Fish Protection | High fish mortality |  | B-fair | III-medium |  | Low Risk |  |  | 4.2 |  | Zyndol | [12 empty] | Currently funded by BPA, could require O&M $ in the future
HATCHERIES | [5 empty] | Bonneville | Hatch house + incubation facility 54' x 156'(new roof 2007) | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Raceway (Battery B) (8 ponds) | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Grating for ponds (foot walks) | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Necessary asset in fair condition
HATCHERIES | [5 empty] | Bonneville | Adult holding pond (lower) updated 1997 | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Adult holding pond (upper) updated 1997 | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Rearing Ponds x 14 (Battery C) | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Rearing Ponds x 14 (Battery D) | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Settling Pond | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition
HATCHERIES | [5 empty] | Bonneville | Fish transport tank (200 gallon) | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte | [12 empty] | Critical asset in fair condition
HATCHERIES | [5 empty] | Cole M Rivers | Hatchery building roofing replacement | [5 empty] | B-fair | III - Medium |  |  |  |  | 4.2 |  | Klatte |  |  | 2011: 100000 |  | Last replaced in 1997
HATCHERIES | [5 empty] | McKenzie | Emergency Power Backup - Office/Service Bldg | [5 empty] | N/A | IV - Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 50000 |  | Backup power for office, freezers, domestic well
HATCHERIES | [5 empty] | McKenzie | Asphalt Paving | [5 empty] | C - Marginal | IV -Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 200000 |  | Replacement or resurfacing of existing
HATCHERIES | [5 empty] | Bonneville | Cushman utility vehicle (white) | [5 empty] | C-marginal | IV - Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 19000 |  | Necessary asset in marginal condition - needs professional maint
HATCHERIES | [5 empty] | Bonneville | Metro Motors micro van | [5 empty] | C-marginal | IV - Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 19000 |  | Necessary asset in marginal condition - needs professional maint
HATCHERIES | [5 empty] | Bonneville | Kiosk 13'x13' (x2) | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 20000 |  | Integral asset in fair condition - needs to be redesigned & updated
HATCHERIES | [5 empty] | Cole M Rivers | Asphalt paving replacement & repair | [5 empty] | C- marginal | IV - Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 500000 |  | Replacement or resurfacing of existing
HATCHERIES | [5 empty] | McKenzie | Repair or Replace Bird Exclusion Netting | [5 empty] | B - Fair | IV - Low |  |  |  |  | 4.3 |  | Klatte |  |  | 2011: 35000 |  | Netting has degraded over the last few years
HATCHERIES | [5 empty] | Cole M Rivers | Public restrooms | [5 empty] | D-poor | V - Minimal |  |  |  |  | 4.4 |  | Klatte |  |  | 2011: 50000 |  | Provide ADA compliant public facilities
HATCHERIES | [5 empty] | Leaburg | Energy efficient windows on hatchery building | [5 empty] | D-poor | V - Minimal |  |  |  |  | 4.4 |  | Klatte |  |  | 2011: 15000 |  | Building repair, infrastructure upgrade
HATCHERIES | [5 empty] | Leaburg | Office building HVAC upgrade | [5 empty] | C- marginal | V - Minimal |  |  |  |  | 4.5 |  | Klatte |  |  | 2011: 50000 |  | Install central HVAC system in offices
HATCHERIES | [5 empty] | Leaburg | Paint hatchery buildings | [5 empty] | C- marginal | V - Minimal |  |  |  |  | 4.5 |  | Klatte |  |  | 2011: 50000 |  | Building maintenance
HATCHERIES | [5 empty] | Leaburg | Office building floor upgrade | [5 empty] | C- marginal | V - Minimal |  |  |  |  | 4.5 |  | Klatte |  |  | 2011: 20000 |  | Update floors in office building
HATCHERIES | [5 empty] | Leaburg | Asbestos removal in freezer room | [5 empty] | C- marginal | V - Minimal |  |  |  |  | 4.5 |  | Klatte |  |  | 2011: 50000 |  | Building maintenance and asbestos removal
HATCHERIES | [5 empty] | Bonneville | Fountain pool & fountains (including three pumps) | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte |  |  | 2011: 5000 |  | Integral asset in fair condition - needs professional maintenance
HATCHERIES | [5 empty] | Bonneville | Flagpoles (x2) | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition
HATCHERIES | [5 empty] | Bonneville | Sturgeon Center (43' x 75') dirt and concrete dam | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Trailer mounted Worthington Compressor 14ED8T 7927 | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition
HATCHERIES | [5 empty] | Bonneville | 175 gallon liberation tank (2) fry tanks | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition
HATCHERIES | [5 empty] | Bonneville | Gardener's building (32' x 18') | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Groundskeeper Utility/Garage 3-Car 1.5 stories 55' 4" x 28' | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #1 (Prop. #26247) 28' x 49', 1.5 stories, 3 bedroom, basement, with garage | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #5 (Prop. #26251) 28' x 49', 1.5 stories, 3 bedroom, basement, with garage | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #2 (Prop. #26248) 45' x 27', 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #3 (Prop. #26249) 45' x 27' , 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #4 (Prop. #26250) 28' x 49', 1.5 stories, 3 bedroom, basement, with garage1.5 stories, | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #6 (Prop. #26252) 45' x 27', 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #7 (Prop. #26253) 45' x 27' 5", 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #9 (Prop. #26254) 45' x 27' 5", 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #10 (Prop. #26255) 45' x 27' 5", 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Residence #11 (Prop. #26256) 45' x 27' 5", 3 bedroom | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Duck pond (64' x 177') dirt and concrete dam | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Integral asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Flatbed Knapheide Stake w/Crysteel Hoist (Boom truck) | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Boom truck bed is 34 years old (replace with boom truck)
HATCHERIES | [5 empty] | Bonneville | Ice-O-Matic ice machine (2) | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition
HATCHERIES | [5 empty] | Bonneville | John Deere tractor, 4-wheel drive with cab, loader & snow blower | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition - needs routine professional maint.
HATCHERIES | [5 empty] | Bonneville | Gravely Pro-Vac Commercial w/vacuum for lawn | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition - needs routine maintenance
HATCHERIES | [5 empty] | Bonneville | Marklift telescoping boom lift | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition - needs routine professional maint.
HATCHERIES | [5 empty] | Bonneville | Kubota Gravely 460 lawn mower | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition - needs routine professional maint.
HATCHERIES | [5 empty] | Bonneville | Toro workman utility cart 2004 | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte | [12 empty] | Necessary asset in fair condition - needs routine professional maint.
HATCHERIES | [5 empty] | Leaburg | Asphalt paving repair and resurface | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte |  |  | 2011: 35000 |  | Repair and sealing of existing asphalt road surfaces
HATCHERIES | [5 empty] | Leaburg | Update domestic well water system | [5 empty] | B-fair | IV - Low |  |  |  |  | 4.6 |  | Klatte |  |  | 2011: 5000 |  | Upgrade components on existing domestic well water system
HATCHERIES | [5 empty] | Bonneville | Vertical Johnson turbine pump (15hp motor) (x2) | [5 empty] | A-good | III - Medium |  |  |  |  | 4.7 |  | Klatte | [12 empty] | Necessary asset in good condition
HATCHERIES | [5 empty] | Bonneville | Maintenance Water system | [5 empty] | A-good | III - Medium |  |  |  |  | 4.7 |  | Klatte | [12 empty] | Necessary asset in good condition
HATCHERIES | [5 empty] | Bonneville | Storm drainage system | [5 empty] | A-good | III - Medium |  |  |  |  | 4.7 |  | Klatte | [12 empty] | Necessary asset in good condition
HATCHERIES | [5 empty] | Bonneville | Truck lift automotive hoist | [5 empty] | A-good | III - Medium |  |  |  |  | 4.7 |  | Klatte | [12 empty] | Necessary asset in good condition
Fish Facilities | [5 empty] | BON | WS Sea lion exclusion devices (SLEDs) | [5 empty] | A | V |  |  |  |  | 5 |  | Hausmann
Fish Facilities | [5 empty] | BON | BI Sea lion exclusion devices (SLEDs) | [5 empty] | A | V |  |  |  |  | 5 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Log booms | [5 empty] | A | V |  |  |  |  | 5 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Lamprey passage structure (LPS) | [5 empty] | A | IV |  |  |  |  | 5 |  | Hausmann
Fish Facilities | [5 empty] | BON | CI Sea lion exclusion devices (SLEDs) | [5 empty] | A | V |  |  |  |  | 5 |  | Hausmann
Fish Facilities | [5 empty] | BON | WS Fish exit trashrack | [5 empty] | B | V |  |  |  |  | 5 |  | Hausmann
HATCHERIES | [5 empty] | Bonneville | Chain link fencing (5' high) | [5 empty] | A-good | IV - Low |  |  |  |  | 5.1 |  | Klatte | [12 empty] | Necessary asset in good condition
HATCHERIES | [5 empty] | Bonneville | Boss Blade snow plow,7'6" trip edge, standard duty | [5 empty] | A-good | IV - Low |  |  |  |  | 5.1 |  | Klatte | [12 empty] | Necessary asset in good condition
HATCHERIES | [5 empty] | Bonneville | Toro Workman, full flatbed with sides 2010 | [5 empty] | A-good | IV - Low |  |  |  |  | 5.1 |  | Klatte | [12 empty] | Necessary asset in good condition - needs routine professional maint.
HATCHERIES | [5 empty] | Bonneville | Drinking fountain (66" square x 32" high) with four spigots and bronze cast salmon artwork | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte | [12 empty] | Integral asset in fair condition
HATCHERIES | [5 empty] | Bonneville | Fish sorter facility | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte | [12 empty] | Asset is being decommissioned
HATCHERIES | [5 empty] | Bonneville | Greenhouse (9' x 16') fiberglass | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte | [12 empty] | Necessary asset in fair condition
HATCHERIES | [5 empty] | Bonneville | Reiff fiberglass fish transport tank (1,000 gal.) | [5 empty] | B-fair | IV - Low |  |  |  |  | 5.2 |  | Klatte | [12 empty] | Necessary asset in fair condition
HATCHERIES | [5 empty] | Cole M Rivers | Domestic water storage tanks | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 50000 |  | Replace existing above-ground water storage tanks
HATCHERIES | [5 empty] | Cole M Rivers | Paint soffits and eaves on hatchery buildings | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 10000 |  | Building repair, requires special equipment for access
HATCHERIES | [5 empty] | Cole M Rivers | Resurface hatchery buildings exterior walls | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 50000 |  | Building repair, maintain structures
HATCHERIES | [5 empty] | Leaburg | Pave abatement/storage yard | [5 empty] | B-fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 25000 |  | Pave earthen areas around abatement ponds for storage
HATCHERIES | [5 empty] | McKenzie | Renew Gutters on Incubation and Service Bldgs. | [5 empty] | C - Marginal | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 10000 |  | Original 1975 gutters
HATCHERIES | [5 empty] | McKenzie | Paint Soffits, Eaves, and Doors all Bldgs | [5 empty] | C - Marginal | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 7500 |  | Good condition but some dry rot
HATCHERIES | [5 empty] | McKenzie | Upgrade Anesthesia Tanks | [5 empty] | B - Fair | III - Medium |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 50000 |  | Change from chemical anestesia to electric
HATCHERIES | [5 empty] | McKenzie | Upgrade Host Sewer System | [5 empty] | B - Fair | V - Minimal |  |  |  |  | 5.2 |  | Klatte |  |  | 2011: 15000 |  | Connect sewage holding tank to lift station and drain field
HATCHERIES | [5 empty] | Bonneville | Irrigation system | [5 empty] | A-good | V - Minimal |  |  |  |  | 5.3 |  | Klatte | [12 empty] | Necessary asset in good condition
Fish Facilities | [5 empty] | BON | JMF AWS pipe | [13 empty] | Hausmann
Fish Facilities | [5 empty] | BON | WS Fish units (1 and 2) | [5 empty] | * | I | [6 empty] | Hausmann
HATCHERIES | [5 empty] | Marion Forks | Hatch House Roof | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 82000 |  | Current roof leaking ad snow damaged, could be water damage under roofing.
HATCHERIES | [5 empty] | Marion Forks | Circular and raceway water valves | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 360000 |  | Valves are original(1951) starting to stick and hard to turn
HATCHERIES | [5 empty] | Marion Forks | Circular pond painting | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 150000 |  | ponds deteriorating cement chipping away, painted 18 of the 48 last year
HATCHERIES | [5 empty] | Marion Forks | Raceway pond painting | [5 empty] | B-fair | III - Medium | [6 empty] | Klatte |  |  | 2011: 120000 |  | cement starting to see some wear
HATCHERIES | [5 empty] | Marion Forks | Asphalt paving replacement & repair | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 42000 |  | Current ashalt cracking and damaged by snowplowing, 2 inch overlay needed
HATCHERIES | [5 empty] | Marion Forks | Horn and Marion intake weirs | [5 empty] | B-fair | III - Medium | [6 empty] | Klatte |  |  | 2011: 30000 |  | Need improve barrier to keep outplanted CHS below water intakes
HATCHERIES | [5 empty] | Marion Forks | New intake screens for Horn and marion Cks. | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 900000 |  | Current screens not NOAA compliant
HATCHERIES | [5 empty] | Marion Forks | Office building heating system upgrade | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 125000 |  | current system origanal 1951
HATCHERIES | [5 empty] | Marion Forks | Hatchery House re-roofing | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 28000 |  | Two of the 3 houses roofs leak, could be damage under roofing
HATCHERIES | [5 empty] | Marion Forks | Lead-based paint assessment | [5 empty] | B-fair | III - Medium | [6 empty] | Klatte |  |  | 2011: 10000 |  | Comprehensive lead paint assessment and management plan
HATCHERIES | [5 empty] | Marion Forks | Asbestos assessment | [5 empty] | B-fair | III - Medium | [6 empty] | Klatte |  |  | 2011: 10000 |  | Comprehensive ACM assessment and management plan
HATCHERIES | [5 empty] | Marion Forks | Painting of hatch house and garage | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 12000 |  | in need of paint, few damages areas
HATCHERIES | [5 empty] | Marion Forks | new windows on hatch house | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 25000 |  | vintage 1951 windows, hard to open and replace
HATCHERIES | [5 empty] | South Santiam | Intake structure screen compliance | [5 empty] | B-fair | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 1-2 million?? |  | Existing intake structure does not meet NOAA requirements
HATCHERIES | [5 empty] | South Santiam | Adult holding pond renovation | [5 empty] | C- marginal | l - High | [6 empty] | Klatte |  |  | 2011: 500k-1 million |  | Replace old pond with 2 separate ponds that are above flood plane.
HATCHERIES | [5 empty] | South Santiam | Serpentine Abatement Pond for AHP | [6 empty] | l - High | [6 empty] | Klatte |  |  | 2011: 250k |  | Will be necessary to meet future DEQ requirements.
HATCHERIES | [5 empty] | South Santiam | Modify raceway effluent plumbing/build PA pond | [5 empty] | B-fair | l - High | [6 empty] | Klatte |  |  | 2011: 300k |  | Will be necessary to meet future DEQ requirements.
HATCHERIES | [5 empty] | South Santiam | Modify adult fish loading system at Foster | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 250k |  | Install 16" pump to transfer fish vs. current manual method
HATCHERIES | [5 empty] | South Santiam | Foster Trap sweep and anesthetic tank upgrade | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 50k |  | Renovate/upgrade 40 year old equipment
HATCHERIES | [5 empty] | South Santiam | Replace 1500 gallon fish liberation truck | [5 empty] | B-fair | III - Medium | [6 empty] | Klatte |  |  | 2011: 80k |  | Replace a 21 year old unit
HATCHERIES | [5 empty] | South Santiam | Replace 1000 gallon fish truck and tank | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 75k |  | Replace a 29 year old unit with new truck and 960 gallon tank - no CDL req.
HATCHERIES | [5 empty] | South Santiam | Replace inflow header pipes on raceways | [5 empty] | C- marginal | III - Medium | [6 empty] | Klatte |  |  | 2011: 15k |  | The current pipes are 40 years old and starting to rust through
HATCHERIES | [5 empty] | South Santiam | Concrete joint and crack repair on raceways | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 50k |  | Seal and repair cracks and seams in raceways
HATCHERIES | [5 empty] | South Santiam | Asphalt sealing and crack repair | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 10k |  | Make repairs to existing asphalt
HATCHERIES | [5 empty] | South Santiam | Shop building roof | [5 empty] | D-poor | III - Medium | [6 empty] | Klatte |  |  | 2011: 25k |  | Replace 22 year old roof, shingles are missing
HATCHERIES | [5 empty] | South Santiam | Forklift | [5 empty] | D-poor | III - Medium | [6 empty] | Klatte |  |  | 2011: 22k |  | Replace 1960 model, parts not avail., used to move fish & euip.
HATCHERIES | [5 empty] | South Santiam | Hatchery building roofs | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte |  |  | 2011: 10k |  | Will need to be replaced in 5-10 years
HATCHERIES | [5 empty] | South Santiam | Hatchery building paint | [5 empty] | B-fair | IV - Low | [6 empty] | Klatte | [12 empty] | Will need to be replaced in 5-10 years | bar: 2011
HATCHERIES | [5 empty] | Willamette | New intake structer | [5 empty] | F-failing | I - High | [6 empty] | Klatte |  |  | 2011: 500000 |  | Sink hole, large debree bypasssing screens and entering facility new screens
HATCHERIES | [5 empty] | Willamette | New pipline @ Dexter | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 200000 |  | Have had leaks. Repaired and was recommended to repalace soon
HATCHERIES | [5 empty] | Willamette | New pipeline @ Willamette | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 250000 |  | We think it is starting to leak. Is underground in a wooded area
HATCHERIES | [5 empty] | Willamette | Roof on shop and hatchhouse | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 50000 |  | Roofs are 30+ years old and in poor shape. Replace with metal
HATCHERIES | [5 empty] | Willamette | New adult holding pond and spawning area | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 150000 |  | Very rustic earthen pond. Received 20,000 to redisign. Then build
HATCHERIES | [5 empty] | Willamette | Ashalt repair and sealing | [5 empty] | D-poor | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 100000 |  | Asphalt is old and crumbling in areas. Need to fix and seal.
HATCHERIES | [5 empty] | Willamette | New grip strut for walk ways | [5 empty] | F-failing | I - High | [6 empty] | Klatte |  |  | 2011: 30000 |  | Walk ways do not meet OR - OSHA standards. Cost for materials only
HATCHERIES | [5 empty] | Willamette | Auto feeding system at Dexter | [5 empty] | New | IV - Low | [6 empty] | Klatte |  |  | 2011: 100000 |  | Would help with work load at Dexter. One man station
HATCHERIES | [5 empty] | Willamette | New Home | [5 empty] | F-failing | IV - Low | [6 empty] | Klatte |  |  | 2011: 200000 |  | Home was removed because of safety isssues, never replaced. Right now employee living off station.
HATCHERIES | [5 empty] | Willamette | Alarms on 40 raceways | [5 empty] | New | I - High | [6 empty] | Klatte |  |  | 2011: 150000 |  | We do not have any alarms on raceways.
HATCHERIES | [5 empty] | Willamette | Pond Repair | [5 empty] | F-failing | II - Medium-High | [6 empty] | Klatte |  |  | 2011: 200000 |  | Replaced 3 bottoms 20 years ago need to rplace the other 7 and walls
Fish Facilities | [5 empty] | TDA | navigation lock | [5 empty] | D | I | [6 empty] | Cordie | [12 empty] | no navlock results in no fish barge transport below BON.
Fish Facilities | [5 empty] | TDA | Fishlock | [5 empty] | D | III | [6 empty] | Cordie | [12 empty] | Alternative to fish units as back-up. Working on rehab.
Fish Facilities | [5 empty] | TDA | Collection channel structure | [5 empty] | C | I | [6 empty] | Cordie | [12 empty] | cannot dewater conduit. Wall under-designed
Fish Facilities | [5 empty] | TDA | fishway grating | [5 empty] | C | I | [6 empty] | Cordie | [12 empty] | end of life expectancy. In process of replacing.
Fish Facilities | [5 empty] | TDA | zebra mussel prep | [5 empty] | C | I | [6 empty] | Cordie | [12 empty] | Need contingency plan if/when they arrive to Col. R
Fish Facilities | [5 empty] | TDA | fishway diffuser valves | [5 empty] | D | IV | [6 empty] | Cordie | [12 empty] | Not operated. Most left full open. CC all closed.
Fish Facilities | [5 empty] | TDA | fishladder expansion joints | [5 empty] | D | III | [6 empty] | Cordie | [12 empty] | working on repair options
Fish Facilities | [5 empty] | TDA | east exit weirs 154-159 | [5 empty] | B | II | [6 empty] | Cordie | [12 empty] | many moving parts. Difficult replacement. Aging.
Fish Facilities | [5 empty] | TDA | north upper diffuser valve | [5 empty] | A | II | [6 empty] | Cordie | [12 empty] | maintained. Minimal moving parts.
Fish Facilities | [5 empty] | TDA | fishway entrance weirs | [5 empty] | A | III | [6 empty] | Cordie | [12 empty] | rehabbed. Spare weirs aval. to both ent. sizes
Fish Facilities | [5 empty] | TDA | count station crowder/brush | [5 empty] | A | III | [6 empty] | Cordie | [12 empty] | maintained. Spare brush motor avail.
Fish Facilities | [5 empty] | TDA | ITS sluicegates | [5 empty] | C | III | [6 empty] | Cordie | [12 empty] | poor condition. FY11 large cap list for rehab or replace.
Fish Facilities | [5 empty] | TDA | ITS endgate | [5 empty] | A | IV | [6 empty] | Cordie | [12 empty] | HSS inspected. Removed when in passage mode.
Fish Facilities | [5 empty] | TDA | spillway | [5 empty] | C | I | [6 empty] | Cordie | [12 empty] | spillway under-designed. Eval underway.
Fish Facilities | [5 empty] | TDA | east fish units | [5 empty] | B | I | [6 empty] | Cordie | [12 empty] | risk assessment completed. Near end of life exp.
Fish Facilities | [5 empty] | TDA | FU generator | [5 empty] | A | I | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | FU excitor | [5 empty] | A | I | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | FU governor | [5 empty] | B | I | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | FU breaker | [5 empty] | A | I | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | FU transformer | [5 empty] | B | II | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | FU stator | [5 empty] | A | I | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | FU rotor | [5 empty] | A | I | [6 empty] | Cordie | [12 empty] | hydroAMP analysis
Fish Facilities | [5 empty] | TDA | North PUD fish turbine | [5 empty] | A | IV | [6 empty] | Cordie | [12 empty] | relatively new unit. High degree of maintenance.

## Sheet2
OR-2 (TD/JD/WC) OR-4 (WV) WA-4 (TD/JD)
OR-2 (R) OR-4 (WV) WA--3 (MSH)
OR-2 (TD/JD) OR-3 (BN) WA-3 (BN) WA-4 (TD/JD)
OR-2 (TD/JD/WC) OR-4 (WV) WA-4 (TD/JD/WC)

## Completed Projects
CRITERIA (Unsat Performance): Life Safety/Economic Impacts/ENS Impact/Legal/Warning Time/Scale of Disruption
FOCUS AREAS LEGEND: Cranes/Fish Facilities/Gates/General/Hydrologic/Jetties/Levees/Pile Dikes/Readiness/Seismic/Stilling Basins/Env Protection (oil spill)
Cost/Budget ($K)
Focus Area | House Delegation | Business Line | FY12 Budget NWP ID/Rank For NWD | NWD RANK | District Rank | Project | Asset(s) Description | Feature Code | RPUID | Phase | Description of Unsatisfactory Performance | Frequency | Consequences | Probability | Consequences of the Unsatisfactory Performance |  |  | Relative Risk | Relative Risk Category | PM or POC | Work Type: Study/ Repairs | $ Source | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | District Strategy | Comments | Contingency Operations Item (Yes/No/ Maybe) | Contingency Operations Description
Gates | OR-4 | Hydro |  |  | 22 | Foster | Dam Spillway Tainter Gates | 04 |  | Construction | Three of four tainter gates (Gates, 1, 2 &3) have experienced localized buckling/deformation of trunnion arms/frames, most likely due to excessive trunnion friction from pin/bushing seizure. Gate 1 has been repaired. | Often | Very High | Very Likely | Critical - gate failure causes uncontrolled loss of pool, flooding downstream, possible loss of life. EC has red-tagged 3 of 4 bays & cannot use gates for flood control. Pool and operational restriction have been implemented. If gates cannot open for flood control, possible overtopping of dam and catastrophic dam failure and loss of life/property downstream. | 3 | 3 | 1.3 | 1 | Dasso | Analysis/P&S/Repair | O&M | 2008: 3500 (70B); 2009: ARRA; Cost/Budget ($K) 2010: 0; Cost/Budget ($K) 2011: 0; Cost/Budget ($K) 2012: TBD | Gates 2,3, and 4 red-tagged and OOS. Dam Safety MFR will stipulate pool and operational restriction until gates repaired. Gate 1 previously repaired. | 08: ranked #1 on UFR list -- seeking ~$850k for misc. O&M activities, including increasing reliability of remaining Gate #3 and operating plan. $500k for analysis and P&S. District developing repair strategy and alternate procurement (i.e. early contractor involvment) strategies. To be completed April 2010. |  | BPA Joint Funded, $100K P&S in FY12 ($28K approp request), $1,000K total const cost.