OFFICIAL COORDINATION REQUEST

FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION DATE- 	June 1, 2011

PROJECT- 	Lower Monumental

RESPONSE DATE- June 9, 2011 – FPOM June meeting

Description of the problem:

At the time the FPP was in draft, it was thought this work would not need the level of outage now deemed necessary.  The contracts have now been awarded and discussions of the work have determined that greater outage demands are required.

Type of outage required:

Emergency Diesel / SQ2 installation contract (LSR Diesel Generator and Switchgear Replacement Projects); the contract work for on the SQ2 portion of this job will require two power house outages. The first outage will be necessary to install temporary power to keep critical systems online while the SQ2 is being replaced.  The second outage will be necessary to remove the temporary power and cut over to the new SQ2 panel.  The CO2 fire suppression is fed out of SQ2 and generation is not permitted unless the CO2 system is active.  The placeholders for this work are in November of 2011. These outages will be all 6 units off line and back feeding the power house via BPA feed.

Impact on facility operation:   The tentative date for cutover to temporary power is November 15 for ½ day to 1 day. The tentative date for reinstatement of permanent power 30 November for a ½ day to 1 day.  All 6 units OOS for this time   We will power the Lower Monumental facility via the 500KV line and backfeeding the power the house from the grid

Length of time for repairs:

November 15 to November 30

Expected impacts on fish passage:  Adult fish counting ends October 31 as all runs have largely passed by this time.  Fish pumps and equipment will operate as normal for maintenance of fish ladder passage conditions. The river flow will be spilled while the units are off line so adult fish attraction flow will change and favor the south ladder.

Overall there is a possibility of minor delay as adult fish follow attraction flow (spill) to the south entrance, but overall impact is likely to be negligible.  All entrances, north ladder and south ladder, will be operated normally thus providing passage opportunity at north, mid, and south river.

The juvenile fish bypass is operated October 1 through December 15 for adult fallback. Juvenile fish numbers in November will be largely composed of shad juveniles with extremely few salmonids in the mix. In that the vast majority of the river flow during the outage will be spill, any juvenile outmigrants will pass via this route.  Under normal November low flow conditions, gas levels will not likely exceed the 120% gas cap.

Current data on fish passage is unavailable for the period of November through March and historic data for this period is unlikely to accurately represent current passage numbers.

Comments from agencies

Final results:

Thank you,