OFFICIAL COORDINATION REQUEST

FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE- 12LWG 010 U3 Exciter Tuning and Generator Model Validation Testing

COORDINATION DATE- July 6, 2012

PROJECT- Lower Granite Lock & Dam

RESPONSE DATE- 12 July 2012 FPOM meeting.

Description of the problem:

Model Validation is required as a subset of rules under the Energy Policy Act and is required at least every 5 years by the Western Electricity Coordinating Council (WECC).  It is required to show the generators will respond to an electrical grid emergency in a way that will prevent the Western grid from collapsing.  It is a relatively new requirement, and is legally binding.

WECC unit Model Validation testing was due by December 31, 2011, but could not be accomplished since the unit has been out of service almost continuously since Jan, 2010 - first to be rewound, and then for cavitation repair.  An attempt was made to complete testing in April, but several portions were not able to be completed, due to equipment failures during the test.  The remaining portions of the test need to be completed, and exciter tuning needs to be completed first, or the test results will be invalidated.  The exciter is what powers the rotor windings of the generator any time it is in service, and is a critical component.

Type of outage required:

A 2 week testing window is being requested between July 23 and August 3, 2012.  The total run time needed to conduct the tests is 16 hours.  The 2 week window includes extra time to accommodate schedule coordination and unexpected delays for repairs.  Outages will only be required when the unit is under test.  During testing, unit priority will be maintained to the maximum extent possible.  Because test equipment must be removed when not in use, 2 eight hour test periods are desired to ensure efficient use of contractor time and specialized test equipment.  Note that transmission lines 1 and 2 Doble Tests are scheduled to take place at Lower Granite from August 13 – 16.

Impact on facility operation:

The unit is estimated to be out of service or under test for less than 16 hours (see the table below), including time for setup and takedown of instrumentation and test equipment when the unit will not be running.

Length of time for tests:

The total sum of the durations at various load levels is estimated as follows:

Expected time of U3 operation inside and outside1% criterion

| Units | No Load (min) | Below 1% (min) | Inside 1% (min) | Above 1% (min) |
| --- | --- | --- | --- | --- |
| 3 | 90 | 300 | 180 | 60 |

Expected impacts on fish passage:

Below are graphs illustrating diel and daily passage of juvenile and adult salmonids at the Lower Granite Dam between July 15 and August 15.  The juvenile charts were created using facility separator records for the years 2010 and 2011. The adult charts utilizes Corps hourly count and daily data for the years 2009, 2010 and 2011.  Very few lamprey were counted during this period and no coho were seen.

Juvenile fish impacts should be minimized if work is conducted between 1400 and 2200 hours, when the fewest number of juvenile fish are present.  Breaking the planned 16 hours of tests into two 8 hour blocks will be possible under this scenario.  The first half of August appears to be the period in which the fewest number of juvenile salmonids are present.  The amount of spill will not change and turbine unit priority will be maintained as much as possible during tests.

Adult fish passage impacts should be minimized if work is conducted during the afternoon and evening hours when fewer numbers of adult fish are present.  If tests are shifted to late night and early morning hours, then juvenile fish passage will be more severely impacted.  Mid to late July appears to be the period in which the fewest number of adult salmonids are present at lower Granite Dam.  As mentioned above, the amount of spill will not change and turbine unit priority will be maintained as much as possible during tests.

A good balanced compromise to minimize both adult and juvenile fish passage impacts appears to be last week of July and the first week of August between 1400 and 2000 hours, especially if only 16 hours of testing are involved.

Comments from agencies

Final results:

Thank you,

John Bailey

509-527-7123