# FPP Change Request Form

Change Request Number & Title: 13BON006 – Table BON-15 PH1 Operating Range

Date Submitted:  12/17/12

Project: BON

Requester Name, Agency: NWP Fisheries Section

Location of Change - FPP Project and Section:

Table BON-15.  Turbine Operating Ranges for B1 updated to include Best Operating Point

Proposed Changes (in track changes to existing section):

See table next page – highlighted text is new.

Justification for Change:

The 2012 Fish Passage Plan provides operating conditions for lower and upper 1% operating conditions for Bonneville Powerhouse 1.  In addition, this year’s plan incorporates suggested operating conditions that have been analyzed and found to be improved fish passage conditions at a specified head.  The Best Operating Point columns are to be utilized when it is possible to improve fish passage mortality through turbines while also maintaining required power requirements.  The best operating point conditions are based on extensive research from the Turbine Survival Program (TSP) that incorporates observational model analysis from ERDC and a relative efficiency analysis for each head developed by HDC based off of these results.  For additional information regarding the work performed by ERDC, see the draft report:  "Bonneville First Powerhouse ERDC Turbine Model BIT Report".  The operation of PH1 up to the Best Operating Point is to be utilized under the guidance of the FPOM when it becomes necessary to increase the capacity of PH1 to reduce flow through PH2 in order to maintain good gatewell fish passage conditions or to maintain spill flow at a level that reduces high dissolved gas levels below the project.

Comments from others:

FPOM 01/24/13:  BPA asked that there be more definitive boundaries as to when the Best Operating Point will be used.

Fredricks requested mid-range tables for PH2.  He also requested change forms for kelt triggers, removal of the STSs related to debris (VBS task group).  Lorz asked if we have the kelt information to make an informed decision about going to PH1 priority for kelt passage in March.

Record of Final Action:

FPOM 01/24/13:  Approved w/ edits.

Table BON- 1.  Bonneville Dam Powerhouse One MGR Turbine Units 1-10 Output (MW) and Discharge (cfs) at the Upper and Lower Limits of the 1% of Peak Efficiency Operating Range and at the Best Operating Point for Heads of 35-70 feet. i

| Head (ft) | Powerhouse One (Units 1-10) |
| --- | --- |
|  | Lower Limit (1%) | Upper Limit (1%) | Best Operating Point ii |
|  | (MW) | (cfs) | (MW) | (cfs) | (MW) | (cfs) |
| 35 | 18.9 | 7,203 | 23.6 | 9,019 | 27.3 | 10,527 |
| 36 | 19.5 | 7,205 | 24.3 | 8,985 | 28.3 | 10,564 |
| 37 | 20.1 | 7,205 | 25.0 | 8,951 | 29.2 | 10,598 |
| 38 | 20.7 | 7,204 | 25.6 | 8,918 | 30.2 | 10,627 |
| 39 | 21.3 | 7,202 | 26.3 | 8,886 | 31.2 | 10,654 |
| 40 | 21.9 | 7,199 | 26.9 | 8,854 | 32.1 | 10,677 |
| 41 | 22.5 | 7,201 | 28.0 | 8,969 | 33.2 | 10,759 |
| 42 | 23.1 | 7,202 | 29.1 | 9,077 | 34.3 | 10,837 |
| 43 | 23.6 | 7,203 | 30.1 | 9,180 | 35.4 | 10,910 |
| 44 | 24.2 | 7,203 | 31.2 | 9,278 | 36.5 | 10,979 |
| 45 | 24.8 | 7,203 | 32.3 | 9,370 | 37.6 | 11,045 |
| 46 | 25.4 | 7,210 | 33.2 | 9,416 | 38.8 | 11,109 |
| 47 | 26.0 | 7,217 | 34.1 | 9,459 | 39.9 | 11,170 |
| 48 | 26.6 | 7,223 | 35.0 | 9,500 | 41.0 | 11,227 |
| 49 | 27.3 | 7,229 | 36.0 | 9,539 | 42.1 | 11,282 |
| 50 | 27.9 | 7,234 | 36.9 | 9,575 | 43.2 | 11,333 |
| 51 | 28.5 | 7,241 | 37.8 | 9,618 | 44.2 | 11,356 |
| 52 | 29.1 | 7,248 | 38.4 | 9,577 | 45.2 | 11,378 |
| 53 | 29.7 | 7,254 | 39.0 | 9,537 | 46.2 | 11,398 |
| 54 | 30.3 | 7,260 | 39.7 | 9,499 | 47.2 | 11,418 |
| 55 | 30.9 | 7,266 | 41.6 | 9,768 | 48.2 | 11,465 |
| 56 | 31.5 | 7,269 | 42.5 | 9,808 | 49.2 | 11,478 |
| 57 | 32.1 | 7,272 | 43.4 | 9,846 | 50.3 | 11,518 |
| 58 | 32.7 | 7,274 | 44.4 | 9,883 | 51.4 | 11,557 |
| 59 | 33.3 | 7,277 | 45.3 | 9,918 | 52.4 | 11,594 |
| 60 | 33.8 | 7,279 | 46.3 | 9,952 | 53.5 | 11,630 |
| 61 | 34.5 | 7296 | 46.9 | 9,930 | 54.3 | 11,610 |
| 62 | 35.1 | 7311 | 47.6 | 9,909 | 55.1 | 11,591 |
| 63 | 35.8 | 7326 | 48.3 | 9,889 | 56.0 | 11,572 |
| 64 | 36.5 | 7340 | 49.0 | 9,868 | 56.6 | 11,519 |
| 65 | 37.1 | 7354 | 49.7 | 9,849 |
| 66 | 37.6 | 7341 | 50.6 | 9,876 |
| 67 | 38.1 | 7329 | 51.4 | 9,902 |
| 68 | 38.6 | 7317 | 52.3 | 9,928 |
| 69 | 39.0 | 7305 | 53.2 | 9,954 |
| 70 | 39.5 | 7294 | 54.1 | 9,979 |

i. Table based on data provided by HDC, June 2000.  Revised 2009 to remove reference to STSs only.  Revised December 2012 to include Best Operating Point.

ii. Best Operating Point (also referred to as Best Geometry) occurs when turbine wicket gates and stay vanes are aligned to provide the maximum water discharge at any operating head (i.e., flow entering the turbine runner encounters the least amount of cross-sectional area of the combined wicket gate and stay vane profiles).  For Bonneville PH1 turbines, the Best Operating Point is above the existing upper limit of the 1% operating range and below the cavitation limit.  From April 01–October 31, turbines will operate within the 1% limits as a hard constraint, unless otherwise coordinated with the region as a special operation for fish passage.