# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title: 	15LGS002 – Unit 1 Low Flow Operations

Date Submitted: 		July 10, 2014

Project: 			Little Goose Lock & Dam

Requester Name, Agency: 	Ann Setter, Corps NWW Operations

Final Action:

FPP Section:	LGS Tables LGS-5, -9, -10, -11, -12.

Justification:	Unit 1 special operating criteria were modified in the 2014 FPP (see change form 14LGS004) to clarify intent is to operate Unit 1 in the upper 1% to push out tailrace eddy from TSW spill.  When flows decrease to <38 kcfs, the project needs flexibility to operate Unit 1 within the full 1% range in order to maintain FOP spill and MOP operations.

However, language in table footnotes state that Unit 1 may operate within full 1% at flow <38 “with only Unit 1 operating”, which is inconsistent with the clarified guidance and with the spill pattern tables at flows 31.5–38 when both Units 1 and 2 are operated below the upper 1% range.

Proposed Change:	Edit footnotes in:

Table LGS-.  Turbine Unit Operating Priority.

a. Unit 1 special operation (section 4.1.2.2 below):  At river flow >38 kcfs, Unit 1 is manually restricted to operate in the upper 25% of the 1% range at 115–125 MW (~16.0-17.5 kcfs).  Assume other units operate approximately uniformly within full 1% range.  When other units are operating at <16.0 kcfs, assume Unit 1 is at the lower end of upper 1% range (~16.0 kcfs).  When average unit discharge is >16.0 kcfs, assume all units operating uniformly.  At low river flow <38 kcfs, Unit 1 may operate within full 1% range.

Tables LGS-, LGS-10, LGS-11, LGS-12 (Spill Pattern Tables)

- Unit 1 manually restricted to upper 1% range (115–125 MW; ~16.0–17.5 kcfs) to disrupt tailrace eddy that forms during spill through SW in Bay 1.  If other units operating uniformly at <16.0 kcfs, assume Unit 1 is at lower end of upper 1% range (~16 kcfs).  If average unit discharge is >16.0 kcfs, assume all units operating uniformly.  During low flows (<38 kcfs), Unit 1 may operate within full 1% range (~11.3–17.5 kcfs).

Comments:

Record of Final Action: