# Fish Passage Plan (FPP) Change Request Form

Change Form # & Title: 	15BON002 – Turbine Maintenance Testing

Date Submitted: 		October 9, 2014

Project: 			Bonneville Dam

Requester Name, Agency: 	Ben Hausmann, BON Fisheries

Final Action:

FPP Section:	BON Section 5.3.4. Turbine Unit Maintenance.

Justification:	30 minutes is not enough time for the control room to test turbine units before maintenance or prior to returning them to operational status.  The increase in turbine testing time to 60 minutes is more realistic and necessary for standard testing procedures to not violate FPP criteria. Additionally, to fully flush fish from the draft tube and immediate tailrace vicinity, a minimum of 3 hours is best with even longer run times being preferred.

Proposed Change:

- 5.3.4. Units may be operationally tested for up to 60 minutes before going into maintenance status by running the unit at speed-no-load and various loads within the 1% range to allow pre-maintenance measurements and testing.  Units will be run for a minimum of 3 hours to flush fish prior to installing tail logs.  Units may be operationally tested after maintenance or repair while remaining in maintenance or forced outage status.  Operational testing may consist of running the unit for up to a cumulative time of 60 minutes within and outside of the 1% range before it is returned to operational status.  Operational testing may deviate from fish priority units and may require water that would otherwise be used for spill if the running unit for reliability is at its 1% lower limit.  Water will be used from powerhouse allocation if possible, and water diverted from spill for operational testing will be minimized to that necessary to maintain and assure generation system reliability.

Comments:

Record of Final Action: