## BON-16
Table BON-16. Bonneville Dam Spill Patterns in Vertical Gate Opening (ft) per Spillbay (0.5 ft = 1 gate stop). a | [19 empty] | NWP POC - Laurie Ebner | Changes for 2017 FPP: |  |  |  | a. This table defines spill patterns in increments of ½ ft total gate opening (1 stop) per row. Spill (kcfs) is calculated as a function of the total gate opening (ft) at forebay elevation 74.0 ft (updated 2007).
BON Spill Patterns - Vertical Gate Opening (ft) per Spillbay | [17 empty] | Total Open | Spill a |  | None
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | (ft) | (kcfs) |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
0.5 | [16 empty] | 0.5 | 1 | 2.3
0.5 | 0.5 | [15 empty] | 0.5 | 1.5 | 3.4
0.5 | 0.5 | [14 empty] | 0.5 | 0.5 | 2 | 4.6
0.5 | 0.5 | [13 empty] | 0.5 | 0.5 | 0.5 | 2.5 | 5.7
0.5 | 0.5 |  | 0.5 | [11 empty] | 0.5 | 0.5 | 0.5 | 3 | 6.9
0.5 | 0.5 |  | 0.5 | 0.5 | [10 empty] | 0.5 | 0.5 | 0.5 | 3.5 | 8
0.5 | 0.5 |  | 0.5 | 0.5 | [8 empty] | 0.5 |  | 0.5 | 0.5 | 0.5 | 4 | 9.2
0.5 | 0.5 |  | 0.5 | 0.5 | [6 empty] | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 4.5 | 10.3
0.5 | 0.5 |  | 0.5 | 0.5 |  |  |  |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 5 | 11.5
0.5 | 0.5 |  | 0.5 | 0.5 |  |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 5.5 | 12.6
0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 6 | 13.8
0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 1 | 0.5 | 6.5 | 14.9
0.5 | 1 | 0.5 | 0.5 | 0.5 |  |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 1 | 0.5 | 7 | 16
0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 1 | 0.5 | 7.5 | 17.2
0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 8 | 18.3
0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 8.5 | 19.5
0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 9 | 20.6
0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 9.5 | 21.8
0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 10 | 22.9
0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 10.5 | 24.1
0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 11 | 25.2
1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 11.5 | 26.3
1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 12 | 27.4
1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 12.5 | 28.6
1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 13 | 29.7
1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 13.5 | 30.8
1 | 1 | 1 | 1 | 0.5 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 14 | 31.9
1 | 1 | 1 | 1 | 0.5 | 0.5 | 1 | 0.5 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 14.5 | 33.1
1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 15 | 34.2
1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 15.5 | 35.3
1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 16 | 36.4
1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 16.5 | 37.6
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 17 | 38.7
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17.5 | 39.8
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 40.9
1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18.5 | 42
1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1 | 19 | 43.2
1 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1 | 19.5 | 44.3
1 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1 | 20 | 45.4
1.5 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1 | 20.5 | 46.5
1.5 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 21 | 47.6
1.5 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | 2 | 1.5 | 21.5 | 48.6
2 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 22 | 49.0193
2 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 22.5 | 50.0769
2 | 2.5 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 23 | 51.1346
2 | 2.5 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2.5 | 2.5 | 2 | 23.5 | 52.1923
2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 24 | 53.4756
2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 24.5 | 54.5332
2 | 2.5 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 25 | 55.5909
2 | 2.5 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 2 | 0 | 2.5 | 2.5 | 2 | 25.5 | 56.6486
2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 26 | 57.9319
2 | 2 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 26.5 | 58.9895
2 | 2.5 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 27 | 60.0472
2 | 2.5 | 2 | 0 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2.5 | 2.5 | 2 | 27.5 | 61.1049
2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 28 | 62.3882
2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 28.5 | 63.4458
2 | 2.5 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2.5 | 2 | 29 | 64.5035
2 | 2.5 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2.5 | 2.5 | 2 | 29.5 | 65.5612
2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 30 | 66.8445
2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2 | 30.5 | 67.9021
2 | 2.5 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2 | 31 | 68.9598
2 | 2.5 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2.5 | 2.5 | 2 | 31.5 | 70.0175
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 32 | 71.3008
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2 | 32.5 | 72.3584
2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2.5 | 2 | 33 | 73.4161
2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 0 | 2 | 2 | 2 | 2.5 | 2.5 | 2 | 33.5 | 74.4738
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 34 | 75.7571
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2 | 34.5 | 76.8147
2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2 | 35 | 77.8724
2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2 | 35.5 | 78.9301
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 36 | 80.2134
2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2 | 36.5 | 81.271
2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2 | 37 | 82.3287
2 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2 | 37.5 | 83.3864
2 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2 | 38 | 84.444
2 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 38.5 | 85.5017
2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 39 | 86.5594
2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 3 | 2.5 | 39.5 | 87.5961
2.5 | 3 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 3 | 2.5 | 40 | 88.6328
2.5 | 3 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 3 | 3 | 40.5 | 89.6695
3 | 3 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 3 | 3 | 41 | 90.7061
3 | 3 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 41.5 | 91.7428
3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 42 | 92.7795
3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 3 | 3 | 3 | 42.5 | 93.8372
3 | 3 | 3 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 3 | 3 | 3 | 43 | 94.8949
3 | 3 | 3 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 43.5 | 95.9525
3 | 3 | 3 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 44 | 97.0102
3 | 3 | 3 | 2.5 | 2.5 | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 44.5 | 98.0679
3 | 3 | 3 | 2.5 | 2.5 | 2 | 2 | 2 | 2.5 | 2 | 2 | 2.5 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 45 | 99.1255
3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2.5 | 2 | 2 | 2.5 | 2 | 2.5 | 2.5 | 3 | 3 | 3 | 45.5 | 100.1832
3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 46.5 | 102.2986
3 | 3 | 3 | 2.5 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 47.5 | 104.3719
3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3 | 3 | 48.5 | 106.4252
3 | 3.5 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3 | 50 | 109.5159
3 | 3.5 | 3.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3 | 50.5 | 110.5
3 | 3.5 | 3.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3 | 51 | 111.6
3 | 3.5 | 3.5 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3 | 51.5 | 112.6
3 | 3.5 | 3.5 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3 | 52 | 113.7
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3 | 52.5 | 114.7
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 3.5 | 3.5 | 53 | 115.7
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 4 | 3.5 | 53.5 | 116.7
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3.5 | 4 | 3.5 | 54 | 117.8
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3.5 | 4 | 3.5 | 54.5 | 118.8
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3.5 | 4 | 3.5 | 55 | 119.8
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 2.5 | 3 | 3 | 3 | 3.5 | 4 | 3.5 | 55.5 | 120.9
3 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 3.5 | 56 | 121.9
3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 3.5 | 56.5 | 122.9
3.5 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 3.5 | 57 | 124
3.5 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 57.5 | 124.9
3.5 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | 58 | 126
3.5 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 58.5 | 127
3.5 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 59 | 128
3.5 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 59.5 | 129
3.5 | 4 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 60 | 130
3.5 | 4 | 4 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 60.5 | 131
4 | 4 | 4 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 61 | 132
4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 4 | 4 | 4 | 61.5 | 133
4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 62 | 134
4 | 4 | 4 | 4 | 3 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 62.5 | 135
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 63 | 136.1
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3 | 4 | 4 | 4 | 4 | 63.5 | 137.1
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 64 | 138.1
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4 | 64.5 | 139.1
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4 | 65 | 140.1
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4 | 65.5 | 141.1
4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 66 | 142.1
4 | 4.5 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 66.5 | 143.1
4 | 4.5 | 4.5 | 4 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 67 | 144
4 | 4.5 | 4.5 | 4 | 3.5 | 3.5 | 3.5 | 3 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 67.5 | 145.1
4 | 4.5 | 4.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 68 | 146.1
4 | 4.5 | 4.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 68.5 | 147.1
4 | 4.5 | 4.5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 69 | 148.1
4 | 4.5 | 4.5 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 69.5 | 149.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4.5 | 4.5 | 4 | 70 | 150.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4.5 | 4 | 70.5 | 151.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4.5 | 4.5 | 4 | 71 | 152.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 71.5 | 153.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 72 | 154.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 3.5 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 72.5 | 155.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 3.5 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 73 | 156.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 3.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 73.5 | 157.1
4 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 74 | 158.1
4 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4 | 74.5 | 159.1
4 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4 | 75 | 160
4 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4 | 75.5 | 161
4 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 76 | 162
4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 76.5 | 163
4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 77 | 163.9
4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4 | 77.5 | 164.9
4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4 | 78 | 165.9
4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4 | 78.5 | 166.8
4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4 | 79 | 167.8
4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 4 | 79.5 | 168.8
4 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 4 | 80 | 169.8
4 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 4 | 80.5 | 170.7
4 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 4 | 81 | 171.7
4 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4 | 4 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 4 | 81.5 | 172.6
4 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 4 | 82 | 173.6
4 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 4 | 82.5 | 174.6
4 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 4 | 83 | 175.6
4 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 4 | 83.5 | 176.5
4 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 4 | 84 | 177.5
4 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 4 | 84.5 | 178.5
4 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 85 | 179.4
4 | 5 | 5 | 5 | 5 | 5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 85.5 | 180.4
4 | 5 | 5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 4.5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 86 | 181.3
4 | 5 | 5 | 5 | 5 | 5 | 4.5 | 5 | 4.5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 86.5 | 182.3
4 | 5 | 5 | 5 | 5 | 5 | 4.5 | 5 | 5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 87 | 183.3
4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4.5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 87.5 | 184.2
4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 88 | 185.2
4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 88.5 | 186.1
4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 4 | 89 | 187.1
4 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 4 | 89.5 | 188
4 | 5.5 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 4 | 90 | 189
4 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 4 | 90.5 | 189.9
4 | 5.5 | 5.5 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 91 | 190.8
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 91.5 | 191.8
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 92 | 192.7
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5.5 | 5 | 5.5 | 5 | 5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 92.5 | 193.7
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5.5 | 5 | 5.5 | 5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 93 | 194.6
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 93.5 | 195.6
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 94 | 196.5
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 4 | 94.5 | 197.5
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 95 | 198.4
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 95.5 | 199.3
4 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 96 | 200.3
4 | 5.5 | 5.5 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 96.5 | 201.2
4 | 5.5 | 5.5 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 97 | 202.1
4 | 5.5 | 5.5 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 97.5 | 203.1
4 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 98 | 204
4 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 98.5 | 204.9
4 | 5.5 | 5.5 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 99 | 205.9
4 | 6 | 5.5 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 5.5 | 4 | 99.5 | 206.8
4 | 6 | 5.5 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 5.5 | 5.5 | 5.5 | 6 | 4 | 100 | 207.7
4 | 6 | 5.5 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 5.5 | 5.5 | 6 | 6 | 4 | 100.5 | 208.6
4 | 6 | 6 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 5.5 | 5.5 | 6 | 6 | 4 | 101 | 209.6
4 | 6 | 6 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 6 | 4 | 101.5 | 210.5
4 | 6 | 6 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 6 | 4.5 | 102 | 211.5
4.5 | 6 | 6 | 5.5 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 6 | 4.5 | 102.5 | 212.4
4.5 | 6 | 6 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 6 | 4.5 | 103 | 213.4
4.5 | 6 | 6 | 6 | 6 | 6 | 5.5 | 6 | 5.5 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6 | 4.5 | 103.5 | 214.3
4.5 | 6 | 6 | 6 | 6 | 6 | 5.5 | 6 | 6 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6 | 4.5 | 104 | 215.2
4.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5.5 | 6 | 6 | 6 | 6 | 6 | 6 | 4.5 | 104.5 | 216.2
4.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4.5 | 105 | 217.1
4.5 | 6 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4.5 | 105.5 | 218
4.5 | 6 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 4.5 | 106 | 218.9
4.5 | 6 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6 | 6 | 4.5 | 106.5 | 219.8
4.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6 | 6 | 4.5 | 107 | 220.7
4.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6 | 6 | 4.5 | 107.5 | 221.6
4.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6 | 6.5 | 4.5 | 108 | 222.6
4.5 | 6.5 | 6 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6 | 6.5 | 4.5 | 108.5 | 223.5
4.5 | 6.5 | 6 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6.5 | 6.5 | 4.5 | 109 | 224.4
4.5 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6 | 6 | 6.5 | 6.5 | 6 | 6 | 6.5 | 6.5 | 4.5 | 109.5 | 225.3
4.5 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6 | 6 | 6.5 | 6.5 | 4.5 | 110 | 226.2
4.5 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 4.5 | 110.5 | 227.1
4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 4.5 | 111 | 228
4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 4.5 | 111.5 | 228.9
4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 4.5 | 112 | 229.9
4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 4.5 | 112.5 | 230.8
4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 4.5 | 113 | 231.7
4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 113.5 | 232.6
5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 114 | 233.6
5 | 6.5 | 6.5 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 114.5 | 234.5
5 | 6.5 | 6.5 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 115 | 235.4
5 | 6.5 | 6.5 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 115.5 | 236.3
5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 116 | 237.2
5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 5 | 116.5 | 238.1
5 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 6.5 | 7 | 5 | 117 | 239
5 | 7 | 6.5 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 6.5 | 7 | 5 | 117.5 | 239.9
5 | 7 | 6.5 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 7 | 7 | 5 | 118 | 240.8
5 | 7 | 7 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 6.5 | 6.5 | 7 | 7 | 6.5 | 6.5 | 7 | 7 | 5 | 118.5 | 241.7
5 | 7 | 7 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 6.5 | 6.5 | 7 | 7 | 5 | 119 | 242.6
5 | 7 | 7 | 6.5 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 6.5 | 7 | 7 | 7 | 5 | 119.5 | 243.5
5 | 7 | 7 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 6.5 | 7 | 7 | 7 | 5 | 120 | 244.4
5 | 7 | 7 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 120.5 | 245.3
5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6.5 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 121 | 246.2
5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 121.5 | 247.1
5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 122 | 248
5 | 7 | 7 | 7 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 122.5 | 248.8
5 | 7 | 7 | 7 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7 | 7 | 7 | 7 | 5 | 123 | 249.7
5 | 7 | 7 | 7 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 5 | 123.5 | 250.6
5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 5 | 124 | 251.5
5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7 | 7 | 7 | 5 | 124.5 | 252.4
5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7 | 7.5 | 7 | 5 | 125 | 253.3
5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7 | 7 | 7.5 | 7.5 | 7 | 7 | 7.5 | 7 | 5 | 125.5 | 254.1
5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7 | 7 | 7.5 | 7 | 5 | 126 | 255
5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7.5 | 7 | 5 | 126.5 | 255.9
5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7 | 7.5 | 7.5 | 7 | 5 | 127 | 256.8
5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 5 | 127.5 | 257.7
5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 5 | 128 | 258.6
5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 5 | 128.5 | 259.5
5 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 5 | 129 | 260.3
5 | 7 | 7.5 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7 | 5 | 129.5 | 261.2
5 | 7 | 7.5 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7 | 5 | 130 | 262.1
5 | 7 | 7.5 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7 | 5 | 130.5 | 262.9
5 | 7 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7 | 5 | 131 | 263.8
5 | 7 | 7.5 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7 | 5 | 131.5 | 264.7
5 | 7 | 7.5 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 5 | 132 | 265.6
5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 7.5 | 7.5 | 5 | 132.5 | 266.5
5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 8 | 7.5 | 5 | 133 | 267.3
5 | 7.5 | 8 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 7.5 | 7.5 | 8 | 8 | 7.5 | 7.5 | 8 | 7.5 | 5 | 133.5 | 268.2
5 | 7.5 | 8 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 7.5 | 7.5 | 8 | 7.5 | 5 | 134 | 269.1
5 | 7.5 | 8 | 7.5 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 7.5 | 8 | 8 | 7.5 | 5 | 134.5 | 269.9
5 | 7.5 | 8 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 7.5 | 8 | 8 | 7.5 | 5 | 135 | 270.8
5 | 7.5 | 8 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8 | 7.5 | 5 | 135.5 | 271.7
5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8 | 7.5 | 5 | 136 | 272.5
5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 5 | 136.5 | 273.4
5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 5 | 137 | 274.3
5 | 7.5 | 8 | 8 | 8.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7.5 | 5 | 137.5 | 275.1
5 | 7.5 | 8 | 8 | 8.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8 | 8 | 8 | 7.5 | 5 | 138 | 276
5 | 7.5 | 8 | 8 | 8.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8 | 7.5 | 5 | 138.5 | 276.9
5 | 7.5 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8 | 7.5 | 5 | 139 | 277.7 |  |  | 277.725 | 10503.625 | 15068.3719 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 15068.3719 | 10503.625
5 | 7.5 | 8 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8 | 7.5 | 5 | 139.5 | 278.6 |  |  | 278.5835 | 10503.625 | 15068.3719 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 15068.3719 | 10503.625
5 | 7.5 | 8 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8 | 8 | 5 | 140 | 279.5 |  |  | 279.4542 | 10503.625 | 15068.3719 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 15939.0784 | 10503.625
5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8 | 8 | 5 | 140.5 | 280.3 |  |  | 280.3249 | 10503.625 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 15939.0784 | 10503.625
5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8.5 | 8 | 5 | 141 | 281.2 |  |  | 281.1834 | 10503.625 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8 | 8 | 8.5 | 8.5 | 8 | 8 | 8.5 | 8 | 5 | 141.5 | 282 |  |  | 282.0419 | 10503.625 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 15939.0784 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8 | 8 | 8.5 | 8 | 5 | 142 | 282.9 |  |  | 282.9004 | 10503.625 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 15939.0784 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8.5 | 8 | 5 | 142.5 | 283.8 |  |  | 283.7588 | 10503.625 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8 | 8.5 | 8.5 | 8 | 5 | 143 | 284.6 |  |  | 284.6173 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 5 | 143.5 | 285.5 |  |  | 285.4758 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 5 | 144 | 286.3 |  |  | 286.3343 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 5 | 144.5 | 287.2 |  |  | 287.1928 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 5 | 145 | 288.1 |  |  | 288.0512 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8 | 5 | 145.5 | 288.9 |  |  | 288.8983 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 146 | 289.7 |  |  | 289.7453 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 146.5 | 290.6 |  |  | 290.5924 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 147 | 291.4 |  |  | 291.4394 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 8.5 | 9 | 8.5 | 8.5 | 8.5 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 147.5 | 292.2865 |  |  | 292.2865 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 8.5 | 9 | 9 | 8.5 | 8.5 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 148 | 293.1335 | Changes made from here down or added. |  | 293.1335 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 8.5 | 9 | 9 | 9 | 8.5 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 148.5 | 293.9806 |  |  | 293.9806 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 149 | 294.8276 |  |  | 294.8276 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8 | 5 | 149.5 | 295.6747 |  |  | 295.6747 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8.5 | 8 | 5 | 150 | 296.5217 |  |  | 296.5217 | 10503.625 | 15939.0784 | 16797.5593 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 151 | 298.2158 |  |  | 298.2158 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 152 | 299.8788 |  |  | 299.8788 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 153 | 301.5418 |  |  | 301.5418 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 154 | 303.2048 |  |  | 303.2048 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 155 | 304.8678 |  |  | 304.8678 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 19307.6 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 10 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 156 | 306.4946 |  |  | 306.4946 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 9 | 10 | 11 | 11 | 10 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 157 | 308.1214 |  |  | 308.1214 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 10 | 10 | 11 | 11 | 10 | 9 | 9 | 9 | 9 | 8.5 | 8 | 5 | 158 | 309.7844 |  |  | 309.7844 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 19307.6 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 10 | 11 | 11 | 11 | 10 | 10 | 9 | 9 | 9 | 8.5 | 8 | 5 | 160 | 313.0742 |  |  | 313.0742 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 20934.4102 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 10 | 11 | 11 | 11 | 11 | 10 | 9 | 9 | 9 | 8.5 | 8 | 5 | 161 | 314.701 |  |  | 314.701 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 10 | 11 | 12 | 11 | 11 | 10 | 9 | 9 | 9 | 8.5 | 8 | 5 | 162 | 316.298 |  |  | 316.298 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 9 | 10 | 11 | 12 | 12 | 11 | 10 | 9 | 9 | 9 | 8.5 | 8 | 5 | 163 | 317.895 |  |  | 317.895 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 10 | 11 | 12 | 12 | 11 | 10 | 9 | 9 | 9 | 8.5 | 8 | 5 | 164 | 319.558 |  |  | 319.558 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 8.5 | 8 | 5 | 165 | 321.221 |  |  | 321.221 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 11 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 8.5 | 8 | 5 | 166 | 322.8478 |  |  | 322.8478 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 11 | 11 | 12 | 12 | 11 | 11 | 10 | 9 | 9 | 8.5 | 8 | 5 | 167 | 324.4746 |  |  | 324.4746 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 22531.4016 | 22531.4016 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 11 | 12 | 12 | 12 | 11 | 11 | 10 | 9 | 9 | 8.5 | 8 | 5 | 168 | 326.0716 |  |  | 326.0716 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 22531.4016 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 11 | 10 | 9 | 9 | 8.5 | 8 | 5 | 169 | 327.6686 |  |  | 327.6686 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 11 | 12 | 13 | 12 | 12 | 11 | 10 | 9 | 9 | 8.5 | 8 | 5 | 170 | 329.2421 |  |  | 329.2421 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 12 | 11 | 10 | 9 | 9 | 8.5 | 8 | 5 | 171 | 330.8157 |  |  | 330.8157 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 10 | 11 | 12 | 13 | 13 | 12 | 11 | 10 | 9 | 9 | 8.5 | 8 | 5 | 172 | 332.4786 |  |  | 332.4786 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 10 | 11 | 12 | 13 | 13 | 12 | 11 | 10 | 10 | 9 | 8.5 | 8 | 5 | 173 | 334.1416 |  |  | 334.1416 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 11 | 12 | 13 | 13 | 12 | 11 | 10 | 10 | 9 | 8.5 | 8 | 5 | 174 | 335.7684 |  |  | 335.7684 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 11 | 12 | 13 | 13 | 12 | 11 | 11 | 10 | 9 | 8.5 | 8 | 5 | 175 | 337.3953 |  |  | 337.3953 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 12 | 13 | 13 | 12 | 11 | 11 | 10 | 9 | 8.5 | 8 | 5 | 176 | 338.9923 |  |  | 338.9923 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 12 | 13 | 13 | 12 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 177 | 340.5892 |  |  | 340.5892 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 22531.4016 | 24104.9354 | 24104.9354 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 12 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 178 | 342.1628 |  |  | 342.1628 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 24104.9354 | 22531.4016 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 179 | 343.7363 |  |  | 343.7363 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 24104.9354 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 13 | 14 | 13 | 13 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 180 | 345.2927 |  |  | 345.2927 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 25661.3728 | 24104.9354 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 13 | 14 | 14 | 13 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 181 | 346.8492 |  |  | 346.8492 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 25661.3728 | 25661.3728 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 13 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 182 | 348.3949 |  |  | 348.3949 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 24104.9354 | 27207.075 | 25661.3728 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 14 | 15 | 15 | 13 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 184 | 351.497 |  |  | 351.497 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 25661.3728 | 27207.075 | 27207.075 | 24104.9354 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 12 | 14 | 15 | 15 | 14 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 185 | 353.0535 |  |  | 353.0535 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 22531.4016 | 25661.3728 | 27207.075 | 27207.075 | 25661.3728 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 13 | 14 | 15 | 15 | 14 | 12 | 11 | 10 | 9 | 8.5 | 8 | 5 | 186 | 354.627 |  |  | 354.627 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 24104.9354 | 25661.3728 | 27207.075 | 27207.075 | 25661.3728 | 22531.4016 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 13 | 14 | 15 | 15 | 14 | 13 | 11 | 10 | 9 | 8.5 | 8 | 5 | 187 | 356.2005 |  |  | 356.2005 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 24104.9354 | 25661.3728 | 27207.075 | 27207.075 | 25661.3728 | 24104.9354 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 11 | 13 | 14 | 15 | 15 | 14 | 13 | 11 | 10 | 9 | 8.5 | 8 | 5 | 187 | 356.2005 |  |  | 356.2005 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 20934.4102 | 24104.9354 | 25661.3728 | 27207.075 | 27207.075 | 25661.3728 | 24104.9354 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 13 | 14 | 15 | 15 | 14 | 13 | 11 | 10 | 9 | 8.5 | 8 | 5 | 188 | 357.7975 |  |  | 357.7975 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 24104.9354 | 25661.3728 | 27207.075 | 27207.075 | 25661.3728 | 24104.9354 | 20934.4102 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 13 | 14 | 15 | 15 | 14 | 13 | 12 | 10 | 9 | 8.5 | 8 | 5 | 189 | 359.3945 |  |  | 359.3945 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 24104.9354 | 25661.3728 | 27207.075 | 27207.075 | 25661.3728 | 24104.9354 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 13 | 14 | 16 | 15 | 14 | 13 | 12 | 10 | 9 | 8.5 | 8 | 5 | 190 | 360.9358 |  |  | 360.9358 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 24104.9354 | 25661.3728 | 28748.4032 | 27207.075 | 25661.3728 | 24104.9354 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 13 | 14 | 16 | 16 | 14 | 13 | 12 | 10 | 9 | 8.5 | 8 | 5 | 191 | 362.4772 |  |  | 362.4772 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 24104.9354 | 25661.3728 | 28748.4032 | 28748.4032 | 25661.3728 | 24104.9354 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 13 | 15 | 16 | 16 | 14 | 13 | 12 | 10 | 9 | 8.5 | 8 | 5 | 192 | 364.0229 |  |  | 364.0229 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 24104.9354 | 27207.075 | 28748.4032 | 28748.4032 | 25661.3728 | 24104.9354 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 13 | 15 | 16 | 16 | 15 | 13 | 12 | 10 | 9 | 8.5 | 8 | 5 | 193 | 365.5686 |  |  | 365.5686 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 24104.9354 | 27207.075 | 28748.4032 | 28748.4032 | 27207.075 | 24104.9354 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 15 | 16 | 16 | 15 | 13 | 12 | 10 | 9 | 8.5 | 8 | 5 | 194 | 367.125 |  |  | 367.125 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 27207.075 | 28748.4032 | 28748.4032 | 27207.075 | 24104.9354 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 15 | 16 | 16 | 15 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 195 | 368.6815 |  |  | 368.6815 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 27207.075 | 28748.4032 | 28748.4032 | 27207.075 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 15 | 17 | 16 | 15 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 196 | 370.2248 |  |  | 370.2248 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 27207.075 | 30291.7186 | 28748.4032 | 27207.075 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 15 | 17 | 17 | 15 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 197 | 371.7681 |  |  | 371.7681 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 27207.075 | 30291.7186 | 30291.7186 | 27207.075 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 16 | 17 | 17 | 15 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 198 | 373.3094 |  |  | 373.3094 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 30291.7186 | 30291.7186 | 27207.075 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 16 | 17 | 17 | 16 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 199 | 374.8507 |  |  | 374.8507 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 30291.7186 | 30291.7186 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 16 | 18 | 17 | 16 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 200 | 376.4024 |  |  | 376.4024 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 30291.7186 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 10 | 12 | 14 | 16 | 18 | 18 | 16 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 201 | 377.9541 |  |  | 377.9541 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 12 | 14 | 16 | 18 | 18 | 16 | 14 | 12 | 10 | 9 | 8.5 | 8 | 5 | 202 | 379.5809 |  |  | 379.5809 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 12 | 14 | 16 | 18 | 18 | 16 | 14 | 12 | 11 | 9 | 8.5 | 8 | 5 | 203 | 381.2077 |  |  | 381.2077 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 14 | 16 | 18 | 18 | 16 | 14 | 12 | 11 | 9 | 8.5 | 8 | 5 | 204 | 382.7812 |  |  | 382.7812 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 25661.3728 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 14 | 16 | 18 | 18 | 16 | 14 | 13 | 11 | 9 | 8.5 | 8 | 5 | 205 | 384.3548 |  |  | 384.3548 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 25661.3728 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 25661.3728 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 15 | 16 | 18 | 18 | 16 | 14 | 13 | 11 | 9 | 8.5 | 8 | 5 | 206 | 385.9005 |  |  | 385.9005 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 27207.075 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 25661.3728 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 15 | 16 | 18 | 18 | 16 | 15 | 13 | 11 | 9 | 8.5 | 8 | 5 | 207 | 387.4462 |  |  | 387.4462 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 27207.075 | 28748.4032 | 31843.3824 | 31843.3824 | 28748.4032 | 27207.075 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 15 | 17 | 18 | 18 | 16 | 15 | 13 | 11 | 9 | 8.5 | 8 | 5 | 208 | 388.9895 |  |  | 388.9895 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 27207.075 | 30291.7186 | 31843.3824 | 31843.3824 | 28748.4032 | 27207.075 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 15 | 17 | 18 | 18 | 17 | 15 | 13 | 11 | 9 | 8.5 | 8 | 5 | 209 | 390.5328 |  |  | 390.5328 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 27207.075 | 30291.7186 | 31843.3824 | 31843.3824 | 30291.7186 | 27207.075 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 15 | 17 | 19 | 18 | 17 | 15 | 13 | 11 | 9 | 8.5 | 8 | 5 | 210 | 392.0992 |  |  | 392.0992 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 31843.3824 | 30291.7186 | 27207.075 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 9 | 11 | 13 | 15 | 17 | 19 | 19 | 17 | 15 | 13 | 11 | 9 | 8.5 | 8 | 5 | 211 | 393.6655 |  |  | 393.6655 | 10503.625 | 15939.0784 | 16797.5593 | 17644.6098 | 20934.4102 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 11 | 13 | 15 | 17 | 19 | 19 | 17 | 15 | 13 | 11 | 9 | 8.5 | 8 | 5 | 212 | 395.3285 |  |  | 395.3285 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 20934.4102 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 20934.4102 | 17644.6098 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 11 | 13 | 15 | 17 | 19 | 19 | 17 | 15 | 13 | 11 | 10 | 8.5 | 8 | 5 | 213 | 396.9915 |  |  | 396.9915 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 20934.4102 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 20934.4102 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 13 | 15 | 17 | 19 | 19 | 17 | 15 | 13 | 11 | 10 | 8.5 | 8 | 5 | 214 | 398.5885 |  |  | 398.5885 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 20934.4102 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 13 | 15 | 17 | 19 | 19 | 17 | 15 | 13 | 12 | 10 | 8.5 | 8 | 5 | 215 | 400.1855 |  |  | 400.1855 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 15 | 17 | 19 | 19 | 17 | 15 | 13 | 12 | 10 | 8.5 | 8 | 5 | 216 | 401.7419 |  |  | 401.7419 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 15 | 17 | 19 | 19 | 17 | 15 | 14 | 12 | 10 | 8.5 | 8 | 5 | 217 | 403.2984 |  |  | 403.2984 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 27207.075 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 16 | 17 | 19 | 19 | 17 | 15 | 14 | 12 | 10 | 8.5 | 8 | 5 | 218 | 404.8397 |  |  | 404.8397 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 27207.075 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 16 | 17 | 19 | 19 | 17 | 16 | 14 | 12 | 10 | 8.5 | 8 | 5 | 219 | 406.381 |  |  | 406.381 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 30291.7186 | 33409.7558 | 33409.7558 | 30291.7186 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 16 | 18 | 19 | 19 | 17 | 16 | 14 | 12 | 10 | 8.5 | 8 | 5 | 220 | 407.9327 |  |  | 407.9327 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 33409.7558 | 33409.7558 | 30291.7186 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 16 | 18 | 19 | 19 | 18 | 16 | 14 | 12 | 10 | 8.5 | 8 | 5 | 221 | 409.4844 |  |  | 409.4844 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 33409.7558 | 33409.7558 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 12 | 14 | 16 | 18 | 20 | 19 | 18 | 16 | 14 | 12 | 10 | 8.5 | 8 | 5 | 222 | 411.0718 |  |  | 411.0718 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 22531.4016 | 25661.3728 | 28748.4032 | 31843.3824 | 34997.2 | 33409.7558 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 14 | 16 | 18 | 20 | 20 | 18 | 16 | 14 | 12 | 10 | 8.5 | 8 | 5 | 224 | 414.2328 |  |  | 414.2328 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 25661.3728 | 28748.4032 | 31843.3824 | 34997.2 | 34997.2 | 31843.3824 | 28748.4032 | 25661.3728 | 22531.4016 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 14 | 16 | 18 | 20 | 20 | 18 | 16 | 14 | 13 | 10 | 8.5 | 8 | 5 | 225 | 415.8063 |  |  | 415.8063 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 25661.3728 | 28748.4032 | 31843.3824 | 34997.2 | 34997.2 | 31843.3824 | 28748.4032 | 25661.3728 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 16 | 18 | 20 | 20 | 18 | 16 | 14 | 13 | 10 | 8.5 | 8 | 5 | 226 | 417.352 |  |  | 417.352 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 28748.4032 | 31843.3824 | 34997.2 | 34997.2 | 31843.3824 | 28748.4032 | 25661.3728 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 16 | 18 | 20 | 20 | 18 | 16 | 15 | 13 | 10 | 8.5 | 8 | 5 | 227 | 418.8977 |  |  | 418.8977 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 28748.4032 | 31843.3824 | 34997.2 | 34997.2 | 31843.3824 | 28748.4032 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 17 | 18 | 20 | 20 | 18 | 16 | 15 | 13 | 10 | 8.5 | 8 | 5 | 228 | 420.441 |  |  | 420.441 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 31843.3824 | 34997.2 | 34997.2 | 31843.3824 | 28748.4032 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 17 | 18 | 20 | 20 | 18 | 17 | 15 | 13 | 10 | 8.5 | 8 | 5 | 229 | 421.9843 |  |  | 421.9843 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 31843.3824 | 34997.2 | 34997.2 | 31843.3824 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 17 | 19 | 20 | 20 | 18 | 17 | 15 | 13 | 10 | 8.5 | 8 | 5 | 230 | 423.5507 |  |  | 423.5507 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 34997.2 | 34997.2 | 31843.3824 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 17 | 19 | 20 | 20 | 19 | 17 | 15 | 13 | 10 | 8.5 | 8 | 5 | 231 | 425.1171 |  |  | 425.1171 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 34997.2 | 34997.2 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 17 | 19 | 21 | 20 | 19 | 17 | 15 | 13 | 10 | 8.5 | 8 | 5 | 232 | 426.732 |  |  | 426.732 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 36612.0762 | 34997.2 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 15 | 17 | 19 | 21 | 21 | 19 | 17 | 15 | 13 | 10 | 8.5 | 8 | 5 | 233 | 428.3468 |  |  | 428.3468 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 33409.7558 | 36612.0762 | 36612.0762 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 17 | 19 | 21 | 21 | 19 | 17 | 15 | 13 | 10 | 8.5 | 8 | 5 | 234 | 429.8882 |  |  | 429.8882 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 30291.7186 | 33409.7558 | 36612.0762 | 36612.0762 | 33409.7558 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 17 | 19 | 21 | 21 | 19 | 17 | 16 | 13 | 10 | 8.5 | 8 | 5 | 235 | 431.4295 |  |  | 431.4295 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 30291.7186 | 33409.7558 | 36612.0762 | 36612.0762 | 33409.7558 | 30291.7186 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 18 | 19 | 21 | 21 | 19 | 17 | 16 | 13 | 10 | 8.5 | 8 | 5 | 236 | 432.9812 |  |  | 432.9812 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 31843.3824 | 33409.7558 | 36612.0762 | 36612.0762 | 33409.7558 | 30291.7186 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 18 | 19 | 21 | 21 | 19 | 18 | 16 | 13 | 10 | 8.5 | 8 | 5 | 237 | 434.5328 |  |  | 434.5328 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 31843.3824 | 33409.7558 | 36612.0762 | 36612.0762 | 33409.7558 | 31843.3824 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 18 | 20 | 21 | 21 | 19 | 18 | 16 | 13 | 10 | 8.5 | 8 | 5 | 238 | 436.1203 |  |  | 436.1203 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 31843.3824 | 34997.2 | 36612.0762 | 36612.0762 | 33409.7558 | 31843.3824 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 18 | 20 | 21 | 21 | 20 | 18 | 16 | 13 | 10 | 8.5 | 8 | 5 | 239 | 437.7077 |  |  | 437.7077 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 31843.3824 | 34997.2 | 36612.0762 | 36612.0762 | 34997.2 | 31843.3824 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 18 | 20 | 22 | 21 | 20 | 18 | 16 | 13 | 10 | 8.5 | 8 | 5 | 240 | 439.3564 |  |  | 439.3564 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 31843.3824 | 34997.2 | 38260.7456 | 36612.0762 | 34997.2 | 31843.3824 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 18 | 20 | 22 | 22 | 20 | 18 | 16 | 13 | 10 | 8.5 | 8 | 5 | 241 | 441.0051 |  |  | 441.0051 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 31843.3824 | 34997.2 | 38260.7456 | 38260.7456 | 34997.2 | 31843.3824 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 20 | 22 | 22 | 20 | 18 | 16 | 13 | 10 | 8.5 | 8 | 5 | 242 | 442.5714 |  |  | 442.5714 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 34997.2 | 38260.7456 | 38260.7456 | 34997.2 | 31843.3824 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 20 | 22 | 22 | 20 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 243 | 444.1378 |  |  | 444.1378 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 34997.2 | 38260.7456 | 38260.7456 | 34997.2 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 21 | 22 | 22 | 20 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 244 | 445.7527 |  |  | 445.7527 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 36612.0762 | 38260.7456 | 38260.7456 | 34997.2 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 21 | 22 | 22 | 21 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 245 | 447.3676 |  |  | 447.3676 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 36612.0762 | 38260.7456 | 38260.7456 | 36612.0762 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 21 | 23 | 22 | 21 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 246 | 449.0564 |  |  | 449.0564 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 36612.0762 | 39949.5694 | 38260.7456 | 36612.0762 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 21 | 23 | 23 | 21 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 247 | 450.7452 |  |  | 450.7452 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 36612.0762 | 39949.5694 | 39949.5694 | 36612.0762 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 22 | 23 | 23 | 21 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 248 | 452.3939 |  |  | 452.3939 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 39949.5694 | 39949.5694 | 36612.0762 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 22 | 23 | 23 | 22 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 249 | 454.0425 |  |  | 454.0425 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 39949.5694 | 39949.5694 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 22 | 24 | 23 | 22 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 250 | 455.7779 |  |  | 455.7779 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 41684.9088 | 39949.5694 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 22 | 24 | 24 | 22 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 251 | 457.5132 |  |  | 457.5132 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 41684.9088 | 41684.9088 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 22 | 25 | 24 | 22 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 252 | 459.3014 |  |  | 459.3014 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 41684.9088 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 10 | 13 | 16 | 19 | 22 | 25 | 25 | 22 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 253 | 461.0897 |  |  | 461.0897 | 10503.625 | 15939.0784 | 16797.5593 | 19307.6 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 13 | 16 | 19 | 22 | 25 | 25 | 22 | 19 | 16 | 13 | 10 | 8.5 | 8 | 5 | 254 | 462.7165 |  |  | 462.7165 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 19307.6 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 13 | 16 | 19 | 22 | 25 | 25 | 22 | 19 | 16 | 13 | 11 | 8.5 | 8 | 5 | 255 | 464.3433 |  |  | 464.3433 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 16 | 19 | 22 | 25 | 25 | 22 | 19 | 16 | 13 | 11 | 8.5 | 8 | 5 | 256 | 465.8997 |  |  | 465.8997 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 16 | 19 | 22 | 25 | 25 | 22 | 19 | 16 | 14 | 11 | 8.5 | 8 | 5 | 257 | 467.4562 |  |  | 467.4562 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 19 | 22 | 25 | 25 | 22 | 19 | 16 | 14 | 11 | 8.5 | 8 | 5 | 258 | 468.9995 |  |  | 468.9995 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 19 | 22 | 25 | 25 | 22 | 19 | 17 | 14 | 11 | 8.5 | 8 | 5 | 259 | 470.5428 |  |  | 470.5428 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 33409.7558 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 20 | 22 | 25 | 25 | 22 | 19 | 17 | 14 | 11 | 8.5 | 8 | 5 | 260 | 472.1302 |  |  | 472.1302 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 33409.7558 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 20 | 22 | 25 | 25 | 22 | 20 | 17 | 14 | 11 | 8.5 | 8 | 5 | 261 | 473.7177 |  |  | 473.7177 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 38260.7456 | 43473.125 | 43473.125 | 38260.7456 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 20 | 23 | 25 | 25 | 22 | 20 | 17 | 14 | 11 | 8.5 | 8 | 5 | 262 | 475.4065 |  |  | 475.4065 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 43473.125 | 43473.125 | 38260.7456 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 20 | 23 | 25 | 25 | 23 | 20 | 17 | 14 | 11 | 8.5 | 8 | 5 | 263 | 477.0953 |  |  | 477.0953 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 43473.125 | 43473.125 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 20 | 23 | 26 | 25 | 23 | 20 | 17 | 14 | 11 | 8.5 | 8 | 5 | 264 | 478.9428 |  |  | 478.9428 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 43473.125 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 8.5 | 11 | 14 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 14 | 11 | 8.5 | 8 | 5 | 265 | 480.7902 |  |  | 480.7902 | 10503.625 | 15939.0784 | 16797.5593 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 10 | 11 | 14 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 14 | 11 | 8.5 | 8 | 5 | 266.5 | 483.3003 |  |  | 483.3003 | 10503.625 | 15939.0784 | 19307.6 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 16797.5593 | 15939.0784 | 10503.625
5 | 8 | 10 | 11 | 14 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 14 | 11 | 10 | 8 | 5 | 268 | 485.8103 |  |  | 485.8103 | 10503.625 | 15939.0784 | 19307.6 | 20934.4102 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 14 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 14 | 11 | 10 | 8 | 5 | 269 | 487.4073 |  |  | 487.4073 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 20934.4102 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 14 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 14 | 12 | 10 | 8 | 5 | 270 | 489.0043 |  |  | 489.0043 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 14 | 12 | 10 | 8 | 5 | 271 | 490.55 |  |  | 490.55 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 17 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 15 | 12 | 10 | 8 | 5 | 272 | 492.0957 |  |  | 492.0957 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 18 | 20 | 23 | 26 | 26 | 23 | 20 | 17 | 15 | 12 | 10 | 8 | 5 | 273 | 493.6474 |  |  | 493.6474 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 31843.3824 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 18 | 20 | 23 | 26 | 26 | 23 | 20 | 18 | 15 | 12 | 10 | 8 | 5 | 274 | 495.199 |  |  | 495.199 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 31843.3824 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 31843.3824 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 18 | 21 | 23 | 26 | 26 | 23 | 20 | 18 | 15 | 12 | 10 | 8 | 5 | 275 | 496.8139 |  |  | 496.8139 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 31843.3824 | 36612.0762 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 31843.3824 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 18 | 21 | 23 | 26 | 26 | 23 | 21 | 18 | 15 | 12 | 10 | 8 | 5 | 276 | 498.4288 |  |  | 498.4288 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 31843.3824 | 36612.0762 | 39949.5694 | 45320.5792 | 45320.5792 | 39949.5694 | 36612.0762 | 31843.3824 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 18 | 21 | 24 | 26 | 26 | 23 | 21 | 18 | 15 | 12 | 10 | 8 | 5 | 277 | 500.1641 |  |  | 500.1641 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 39949.5694 | 36612.0762 | 31843.3824 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 10 | 12 | 15 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 15 | 12 | 10 | 8 | 5 | 278 | 501.8995 |  |  | 501.8995 | 10503.625 | 15939.0784 | 19307.6 | 22531.4016 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 11 | 12 | 15 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 15 | 12 | 10 | 8 | 5 | 279 | 503.5263 |  |  | 503.5263 | 10503.625 | 15939.0784 | 20934.4102 | 22531.4016 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 22531.4016 | 19307.6 | 15939.0784 | 10503.625
5 | 8 | 11 | 12 | 15 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 15 | 12 | 11 | 8 | 5 | 280 | 505.1531 |  |  | 505.1531 | 10503.625 | 15939.0784 | 20934.4102 | 22531.4016 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 22531.4016 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 15 | 12 | 11 | 8 | 5 | 281 | 506.7266 |  |  | 506.7266 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 22531.4016 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 11 | 8 | 5 | 282 | 508.3001 |  |  | 508.3001 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 11 | 8 | 5 | 283 | 509.8415 |  |  | 509.8415 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 18 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 16 | 13 | 11 | 8 | 5 | 284 | 511.3828 |  |  | 511.3828 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 19 | 21 | 24 | 26 | 26 | 24 | 21 | 18 | 16 | 13 | 11 | 8 | 5 | 285 | 512.9492 |  |  | 512.9492 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 19 | 21 | 24 | 26 | 26 | 24 | 21 | 19 | 16 | 13 | 11 | 8 | 5 | 286 | 514.5155 |  |  | 514.5155 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 19 | 22 | 24 | 26 | 26 | 24 | 21 | 19 | 16 | 13 | 11 | 8 | 5 | 287 | 516.1642 |  |  | 516.1642 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 19 | 22 | 24 | 26 | 26 | 24 | 22 | 19 | 16 | 13 | 11 | 8 | 5 | 288 | 517.8129 |  |  | 517.8129 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 41684.9088 | 45320.5792 | 45320.5792 | 41684.9088 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 19 | 22 | 25 | 26 | 26 | 24 | 22 | 19 | 16 | 13 | 11 | 8 | 5 | 289 | 519.6011 |  |  | 519.6011 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 41684.9088 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 19 | 22 | 25 | 26 | 26 | 25 | 22 | 19 | 16 | 13 | 11 | 8 | 5 | 290 | 521.3893 |  |  | 521.3893 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 20 | 22 | 25 | 26 | 26 | 25 | 22 | 19 | 16 | 13 | 11 | 8 | 5 | 291 | 522.9768 |  |  | 522.9768 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 20 | 22 | 25 | 26 | 26 | 25 | 22 | 20 | 16 | 13 | 11 | 8 | 5 | 292 | 524.5642 |  |  | 524.5642 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 20 | 23 | 25 | 26 | 26 | 25 | 22 | 20 | 16 | 13 | 11 | 8 | 5 | 293 | 526.253 |  |  | 526.253 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 43473.125 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 20 | 23 | 25 | 26 | 26 | 25 | 23 | 20 | 16 | 13 | 11 | 8 | 5 | 294 | 527.9419 |  |  | 527.9419 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 43473.125 | 45320.5792 | 45320.5792 | 43473.125 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 25 | 23 | 20 | 16 | 13 | 11 | 8 | 5 | 295 | 529.7893 |  |  | 529.7893 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
5 | 8 | 11 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 11 | 8 | 5 | 296 | 531.6368 |  |  | 531.6368 | 10503.625 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
6 | 8 | 11 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 11 | 8 | 5 | 297 | 533.5081 |  |  | 533.5081 | 12374.9472 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 10503.625
6 | 8 | 11 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 11 | 8 | 6 | 298 | 535.3794 |  |  | 535.3794 | 12374.9472 | 15939.0784 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 12374.9472
6 | 9 | 11 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 11 | 8 | 6 | 299 | 537.0849 |  |  | 537.0849 | 12374.9472 | 17644.6098 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 15939.0784 | 12374.9472
6 | 9 | 11 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 11 | 9 | 6 | 300 | 538.7905 |  |  | 538.7905 | 12374.9472 | 17644.6098 | 20934.4102 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 17644.6098 | 12374.9472
6 | 9 | 12 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 11 | 9 | 6 | 301 | 540.3875 |  |  | 540.3875 | 12374.9472 | 17644.6098 | 22531.4016 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 20934.4102 | 17644.6098 | 12374.9472
6 | 9 | 12 | 13 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 12 | 9 | 6 | 302 | 541.9844 |  |  | 541.9844 | 12374.9472 | 17644.6098 | 22531.4016 | 24104.9354 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 13 | 12 | 9 | 6 | 303 | 543.5409 |  |  | 543.5409 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 24104.9354 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 16 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 14 | 12 | 9 | 6 | 304 | 545.0973 |  |  | 545.0973 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 28748.4032 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 17 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 16 | 14 | 12 | 9 | 6 | 305 | 546.6406 |  |  | 546.6406 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 28748.4032 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 17 | 20 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 17 | 14 | 12 | 9 | 6 | 306 | 548.184 |  |  | 548.184 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 34997.2 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 17 | 21 | 23 | 26 | 26 | 26 | 26 | 23 | 20 | 17 | 14 | 12 | 9 | 6 | 307 | 549.7988 |  |  | 549.7988 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 34997.2 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 17 | 21 | 23 | 26 | 26 | 26 | 26 | 23 | 21 | 17 | 14 | 12 | 9 | 6 | 308 | 551.4137 |  |  | 551.4137 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 39949.5694 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 23 | 21 | 17 | 14 | 12 | 9 | 6 | 309 | 553.149 |  |  | 553.149 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 39949.5694 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
6 | 9 | 12 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 12 | 9 | 6 | 310 | 554.8844 |  |  | 554.8844 | 12374.9472 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
7 | 9 | 12 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 12 | 9 | 6 | 311 | 556.6941 |  |  | 556.6941 | 14184.6446 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 12374.9472
7 | 9 | 12 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 12 | 9 | 7 | 312 | 558.5038 |  |  | 558.5038 | 14184.6446 | 17644.6098 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 14184.6446
7 | 10 | 12 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 12 | 9 | 7 | 313 | 560.1668 |  |  | 560.1668 | 14184.6446 | 19307.6 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 17644.6098 | 14184.6446
7 | 10 | 12 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 12 | 10 | 7 | 314 | 561.8298 |  |  | 561.8298 | 14184.6446 | 19307.6 | 22531.4016 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 19307.6 | 14184.6446
7 | 10 | 13 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 12 | 10 | 7 | 315 | 563.4033 |  |  | 563.4033 | 14184.6446 | 19307.6 | 24104.9354 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 22531.4016 | 19307.6 | 14184.6446
7 | 10 | 13 | 14 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 13 | 10 | 7 | 316 | 564.9768 |  |  | 564.9768 | 14184.6446 | 19307.6 | 24104.9354 | 25661.3728 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 24104.9354 | 19307.6 | 14184.6446
7 | 10 | 13 | 15 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 14 | 13 | 10 | 7 | 317 | 566.5225 |  |  | 566.5225 | 14184.6446 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 25661.3728 | 24104.9354 | 19307.6 | 14184.6446
7 | 10 | 13 | 15 | 17 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 15 | 13 | 10 | 7 | 318 | 568.0682 |  |  | 568.0682 | 14184.6446 | 19307.6 | 24104.9354 | 27207.075 | 30291.7186 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 14184.6446
7 | 10 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 17 | 15 | 13 | 10 | 7 | 319 | 569.6199 |  |  | 569.6199 | 14184.6446 | 19307.6 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 30291.7186 | 27207.075 | 24104.9354 | 19307.6 | 14184.6446
7 | 10 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 10 | 7 | 320 | 571.1716 |  |  | 571.1716 | 14184.6446 | 19307.6 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 19307.6 | 14184.6446
8 | 10 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 10 | 7 | 321 | 572.926 |  |  | 572.926 | 15939.0784 | 19307.6 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 19307.6 | 14184.6446
8 | 10 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 10 | 8 | 322 | 574.6804 |  |  | 574.6804 | 15939.0784 | 19307.6 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 19307.6 | 15939.0784
8 | 11 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 10 | 8 | 323 | 576.3072 |  |  | 576.3072 | 15939.0784 | 20934.4102 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 19307.6 | 15939.0784
8 | 11 | 13 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 11 | 8 | 324 | 577.934 |  |  | 577.934 | 15939.0784 | 20934.4102 | 24104.9354 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 20934.4102 | 15939.0784
8 | 11 | 14 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 13 | 11 | 8 | 325 | 579.4905 |  |  | 579.4905 | 15939.0784 | 20934.4102 | 25661.3728 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 24104.9354 | 20934.4102 | 15939.0784
8 | 11 | 14 | 15 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 14 | 11 | 8 | 326 | 581.0469 |  |  | 581.0469 | 15939.0784 | 20934.4102 | 25661.3728 | 27207.075 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 15 | 14 | 11 | 8 | 327 | 582.5883 |  |  | 582.5883 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 27207.075 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 18 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 16 | 14 | 11 | 8 | 328 | 584.1296 |  |  | 584.1296 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 31843.3824 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 19 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 18 | 16 | 14 | 11 | 8 | 329 | 585.696 |  |  | 585.696 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 31843.3824 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 19 | 21 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 19 | 16 | 14 | 11 | 8 | 330 | 587.2623 |  |  | 587.2623 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 36612.0762 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 19 | 22 | 24 | 26 | 26 | 26 | 26 | 24 | 21 | 19 | 16 | 14 | 11 | 8 | 331 | 588.911 |  |  | 588.911 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 36612.0762 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 19 | 22 | 24 | 26 | 26 | 26 | 26 | 24 | 22 | 19 | 16 | 14 | 11 | 8 | 332 | 590.5597 |  |  | 590.5597 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 41684.9088 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 41684.9088 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 11 | 14 | 16 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 16 | 14 | 11 | 8 | 334 | 594.1361 |  |  | 594.1361 | 15939.0784 | 20934.4102 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 12 | 14 | 16 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 16 | 14 | 11 | 8 | 335 | 595.7331 |  |  | 595.7331 | 15939.0784 | 22531.4016 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 20934.4102 | 15939.0784
8 | 12 | 14 | 16 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 16 | 14 | 12 | 8 | 336 | 597.3301 |  |  | 597.3301 | 15939.0784 | 22531.4016 | 25661.3728 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 22531.4016 | 15939.0784
8 | 12 | 15 | 16 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 16 | 14 | 12 | 8 | 337 | 598.8758 |  |  | 598.8758 | 15939.0784 | 22531.4016 | 27207.075 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 25661.3728 | 22531.4016 | 15939.0784
8 | 12 | 15 | 16 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 16 | 15 | 12 | 8 | 338 | 600.4215 |  |  | 600.4215 | 15939.0784 | 22531.4016 | 27207.075 | 28748.4032 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 27207.075 | 22531.4016 | 15939.0784
8 | 12 | 15 | 17 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 16 | 15 | 12 | 8 | 339 | 601.9648 |  |  | 601.9648 | 15939.0784 | 22531.4016 | 27207.075 | 30291.7186 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 28748.4032 | 27207.075 | 22531.4016 | 15939.0784
8 | 12 | 15 | 17 | 19 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 17 | 15 | 12 | 8 | 340 | 603.5081 |  |  | 603.5081 | 15939.0784 | 22531.4016 | 27207.075 | 30291.7186 | 33409.7558 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 30291.7186 | 27207.075 | 22531.4016 | 15939.0784
8 | 12 | 15 | 17 | 20 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 19 | 17 | 15 | 12 | 8 | 341 | 605.0956 |  |  | 605.0956 | 15939.0784 | 22531.4016 | 27207.075 | 30291.7186 | 34997.2 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 33409.7558 | 30291.7186 | 27207.075 | 22531.4016 | 15939.0784
8 | 12 | 15 | 17 | 20 | 22 | 25 | 26 | 26 | 26 | 26 | 25 | 22 | 20 | 17 | 15 | 12 | 8 | 342 | 606.683 |  |  | 606.683 | 15939.0784 | 22531.4016 | 27207.075 | 30291.7186 | 34997.2 | 38260.7456 | 43473.125 | 45320.5792 | 45320.5792 | 45320.5792 | 45320.5792 | 43473.125 | 38260.7456 | 34997.2 | 30291.7186 | 27207.075 | 22531.4016 | 15939.0784