# Fish Passage Plan (FPP) Change Form

**Change Form # & Title**: 21LMN006 – RSW Spill Rates

**Date Submitted**: 2 September 2021

**Project**: Lower Monumental Dam

**Requester Name, Agency**: Lisa Wright, Corps

**Final Action:**

**FPP Section**:

Chapter 7 LMN, section 2.3.2.6. RSW Operating Criteria.

**Justification for Change**:

FPOM approved adding Lower Granite RSW spill rates vs forebay elevation in Change Form 21LWG006 on 9/9/21 and requested adding the same information for the other Snake projects.

**Proposed Change**: *(see following pages for edits to existing FPP in track changes)*

**Comments**:

**Record of Final Action**:

Proposed Change:

**2.3.2.6. Removable Spillway Weir (RSW).**

Lower Monumental Dam has one removable spillway weir (RSW) in spillbay 8 that, when open, provides a surface route for fish passage. The RSW can be opened and closed from the control room.

The spill rate through the RSW is a function of the forebay elevation – as the pool elevation increases, more water is spilled over the RSW:

|  |  |
| --- | --- |
| **LMN Forebay Elevation (ft)** | **RSW Spill Rate (kcfs)** |
| 537 | 6.7 |
| 537.5 | 7.1 |
| 538 | 7.5 |
| 538.5 | 8.0 |
| 539 | 8.5 |
| 539.5 | 9.0 |
| 540 | 9.5 |

The RSW will be in the raised position and operational during spill for juvenile fish passage (**Appendix E**)and spill for adult steelhead (**section 2.2**):

Raise the spill gate to where it does not touch flow passing down the RSW.

During high flows, if the Northwest River Forecast Center (NWRFC) inflow forecast for Lower Monumental is above 200 kcfs, initiate aggressive forebay debris removal to avoid impeding RSW operation. Coordinate with RCC and CENWW-OD-T. If inflow exceeds 260 kcfs, the upstream river gauge flow is increasing, and the NWRFC inflow forecast for Lower Monumental is above 300 kcfs, stow the RSW (complete rotation to the landing pad).

During summer spill (June 21-August 31), when daily average total project outflow is less than 30 kcfs and inflow is forecasted to remain below 30 kcfs for at least three days on a declining hydrograph, close the RSW and spill according to patterns with no RSW in **Table LMN-9**. If daily average project outflow subsequently increases above 30 kcfs and inflow is forecasted to remain above 30 kcfs for at least three days, re-open the RSW.Continue to open and close the RSW according to these criteria throughout summer spill.

Outside of spill season when transport is occurring, the RSW may be operated for short periods upon request by the Project Biologist through CENWW if it appears the juvenile transportation facility and barge holding capacities will be exceeded, as defined in the *Juvenile Fish Transportation Plan* (**Appendix B**).