## NWW
Project | Location | Work Item | Comment - Red highlighted items currently affect meeting FPP criteria | NWW | NOAA | USFWS | CRITFC | WDFW | ODFW | IDFG | Average
L Monumental | Spillway | Spillbay 3 | Bay 3 currently tagged OOS due to failed test. | 5 | 5 | 5 | 5 | 5 |  | 5 | 5
McNary | Oregon Fishway | Repair/replace three south shore AWS pumps. | Condition of pumps results in being off line often for repairs. Pumps 1 & 3 currently OOS requiring closing of some entrances to maintain passage criteia | 5 | 5 | 5 | 5 | 5 |  | 5 | 5
L Goose | Forebay | Repair debris boom | Ineffective design collects debris and allows debris to reach powerhouse where it increases risk of injury and mortality for juvenile fish | 5 | 5 | 4 | 5 | 5 |  | 4 | 4.6667
McNary | Spillway | Rehabe/replace spillway cranes and hoists 6&7 | Cranes and hoists 6&7 underrated for lifting requirements and often OOS for repairs because of age and condition | 5 | 4 | 4 | 5 | 5 |  | 5 | 4.6667
All | Bypass system | Critical spare parts | Lack of sufficient spare parts required juvenile passage to be in emergency bypass March 2021 | 4 | 5 | 4 | 4 | 5 |  | 5 | 4.5
McNary | Spillway | Add hoists to spillbays 2 and 19 | Spillbays 2 and 19 do not contain hoists and can only be operated using two spillway cranes. | 5 | 3 | 4 | 5 | 5 |  | 5 | 4.5
All | Fishways | Support for fishway temperature monitoring | CRIFM funds were provided for installation of temperature sensors that provide real-time posting of fishway temperatures but no funding has been identified for continued O&M. | 4 | 4 | 5 | 4 | 4 |  | 5 | 4.3333
Ice Harbor | Powerhouse deck | Repair/replace trash rake | Failed inspection spring 2021 | 5 | 5 | 4 | 4 | 4 |  | 5 | 4.5
L Monumental | Fishway | Fishway cooling system | Analysis shows potential to cool fishways 1-4 degrees F during warm water periods using structures similar to those installed at Little Goose and Lower Granite dams | 4 | 5 | 5 | 4 | 4 |  | 5 | 4.5
Lower Granite | Fishway | Rehad/replace fishway AWS pumps | Age and condition of pumps create high risk of failure. | 4 | 4 | 4 | 4 | 4 |  | 5 | 4.1667
Lower Granite | Fishway | Modify adult trap turnpool gate | Convert to lift gate to allow fish to pass upstream without transiting the adult trap at night and weekends during passage season | 4 | 5 | 3 | 4 | 4 |  | 4 | 4
Ice Harbor | South fishway | AWS pump rehab | Aging pumps have high risk of failure | 3 | 4 | 4 | 4 | 4 |  | 4 | 3.8333
L Goose | North shore | Replace north shore jetty | Lost during high flows, protects north shore fishway entrance from shore eddy | 3 | 5 | 3 | 4 | 3 |  | 5 | 3.8333
L Goose | Fishway | Replace fishway control system | Fishway entrances operate in manual mode only, requiring regular inspections and manual adjustments to maintain fishway criteria | 4 | 4 | 5 | 3 | 3 |  | 4 | 3.8333
Lower Granite | Fishways | Rehad/replace fishway entrances. NSE1 and NSE2 are showing cracks in the concrete | Age and condition of fishway entrances create relatively high risk for failure | 4 | 4 | 4 | 3 | 4 |  | 4 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Replace transverse stoplog guides. | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all transverse stoplogs. | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; replace rotovalves, slide gates | Project cannot currently dewater south shore fishway to affect repairs. See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all floating weirs and guides | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | JFF | Add tailrace bird wires |  | 4 | 5 | 4 | 5 | 5 * |  | 5 | 3.8333
McNary | Oregon Fishway | Replace diffuser gratings and grate supports | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 5 | 4 | 3 | 4 |  | 3 | 3.8333
Ice Harbor | Fishways | Entrance hoists and controls replacement | Hoists have failed causing fishway to be temporarily closed and out of criteria | 3 | 4 | 5 | 3 | 3 |  | 4 | 3.6667
Lower Granite | Barges | Improve degassing system on 2000 barges | Current pumping system is inadequate to degass river water during periods of high TDG | 4 | 5 | 4 | 3 | 5 |  | 1 | 3.6667
L Monumental | Forebay | Install shear boom to move debris to spillway | Debris can enter juvenile bypass system, risking injury and mortality to juvenile salmonids | 3 | 5 | 4 | 3 | 3 |  | 3 | 3.5
Lower Granite | Fishway | Correct Control System Programing malfunction | Control system is not accurate, requiring regular inspections and manual adjustments to maintain fishway criteria | 4 | 3 | 5 | 3 | 3 |  | 3 | 3.5
L Monumental | JFF | Hoist system for tailrace tail screens | Current system is insufficient and unsafe to operate | 3 | 3 | 4 | 3 | 4 |  | 3 | 3.3333
L Goose | Fishway | Re-design fish count station | Turbulence interferes with accurate fish counting | 4 | 2 | 4 | 3 | 4 |  | 2 | 3.1667
L Monumental | JFF | Primary Dewaterer repairs | Worn brass nuts, missing motor, weir held in place with chain | 3 | 3 | 4 | 3 | 3 |  | 3 | 3.1667
McNary | JFF | Replace outfall sprinklers | Sprinklers and supply line lost during high flows in 2018 | 3 | 4 | 4 | 1 | 2 |  | 4 | 3
Ice Harbor | Forebay | Ladder exit debris booms | Current log booms are old and are prone to failure with east winds | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
Ice Harbor | Juvenile fish channel | Expansion of air burst cleaning system under inclined screen | Material purchase needed to keep screens clear of debris | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
L Goose | Fishway | Replace diffuser grating and support beams |  | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
L Goose | Collection channel | Repair/replace corroded outer steel orifice pipe with stainless steal | Orifices have failed mid-season causing them to be closed until winter maintenance period | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
L Goose | Collection channel | Repair orifice valve cylinders |  | 3 | 3 | 2 | 3 | 3 |  | 3 | 2.8333
L Monumental | Fishway | Repair /replace expansion joint seals | Leaks from fishway create saftey risks, particularily during cold weather when ice forms on walkways | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
Lower Granite | Fishway | Install/replace velocity meter in channel | Current system not working, provides inaccurate readings | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
Lower Granite | Fishway | Shad exclusion/ deterrent devise | Reduce adult shad in adult trap and fishway to reduce stress and crowding to salmon migrants, reduce risk from dead shad collecting on gates and screens and potentially reduce shad population upstream of Lower Granite Dam | 3 | 3 | 2 | 3 | 3 |  | 3 | 2.8333
L Goose | Fishway | Repair /replace expansion joint seals | Leaks from fishway create saftey risks, particularily during cold weather when ice forms on walkways | 3 | 3 | 3 | 2 | 3 |  | 2 | 2.6667
Ice Harbor | Fish count station | Air motors for window brushes | $2500 per motor | 3 | 3 | 3 | 2 | 3 |  | 1 | 2.5
McNary | Oregon Fishway | Permanently close floating orifice gates not used | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 3 | 2 | 2 | 3 | 3 |  | 2 | 2.5
Ice Harbor | Fishways | Replace missing/broken depth gauages |  | 2 | 4 | 2 | 2 | 2 |  | 1 | 2.1667
Ice Harbor | Juvenile fish channel | Spare actuator for water regulating weirs |  | 2 | 3 | 2 | 2 | 2 |  | 1 | 2
Lower Granite | JFF | Complete Phase 1a modifications and resolve programing issues. | PDW/JBS | 2 | 2 | 3 | 2 | 2 |  | 1 | 2
Lower Granite | Fishway | Permanently close floating orifice gates not used | Reduce leaking and annual maintenenace of stoplogs | 2 | 2 | 3 | 2 | 2 |  | 1 | 2
Lower Granite | Fishway | NSE, SSE, and NPE local depth indication | Current system not working, provides inaccurate readings | 2 | 2 | 2 | 2 | 2 |  | 1 | 1.8333
Lower Granite | Fishway | Relocate south shore tailwater elevation sensor |  | 2 | 2 | 2 | 2 | 2 |  | 1 | 1.8333
Ice Harbor | Fishway | Shad exclusion/deterrent devise | Reduce adult shad passing Ice Harbor Dam, potentially reducing shad population in the Snake River | 1 | 1 | 1 | 3 | 1 |  | 1 | 1.3333
All ranking is 1-5, similar to SCT.
1 = lowest 5 = highest priority
indicates "defer to Corps"

## NWP
Project | Work Package Title | Condition / Description of Unsatisfactory Performance | Consequences of the Unsatisfactory Performance (Budget Justification) | NWP | NOAA | USFWS | CRITFC | WDFW | ODFW | IDFG | Average
John Day | AWS Rehab Remaining 2 Fish Unit Turbine Pumps (SAP Name: Fish HYD Pumps U1 & U2 Rehabilitiation?) | Age of turbines and possibility of failure leads to requirement for rehab. All 3 installed at same time, one has failed and pump 2 is near failure. One remaining functional pump will likely fail soon. | Critical to the Fish Passage Plan and keep John Day within adult passage criteria under the FCRPS BiOp to provide safe passage for Esa listed fish and resident fish species. The units are more than 50 years old and are currently showing major wear with leaking gearbox seals and worn guide bearings. | 4 | 5 | 5 | 5 | 5 |  | 5 | 4.8333
John Day | Bonneville Hatchery Well Field | Hatchery well field has iron bacteria problem and local well gravel pack silting. | Critical - loss of fish production, failure to meet John Day Mitigation obligations | 5 | 3 | 5 | 5 | 5 |  | 2 | 4.1667
The Dalles | Fishway Automation | Critical components are past useful life and unsupported by OEM. Originally installed fiber optic cable is failing. Replacement parts are no longer available for purchase. Procure and install new fishway automation for all entrance and exit weirs. | This fishway passes approx 80% of total adult fish passage upstream on the Columbia River. If water levels in the fishladder cannot be regulated then fish passage will be negatively impacted. Seven ESA listed salmonid species pass through this system. | 4 | 4 | 4 | 4 | 4 |  | 5 | 4.1667
The Dalles | Fishway Arc Flash Mitigation | Several pieces of equipment have high arc flash incident energies (Cat 4). Arc Flash Hazard Analysis completed in March 2015 by HDR identified several pieces of equipment with high arc flash incident energies. The analysis provided recommended mitigation to lower the arc flash incident energy to a safe level for personnel. The majority of the recommended mitigation is being completed under a power funded contract; however, there is equipment remaining that requires mitigation which can not be power funded. The equipment with high arc flash incident energies are at substations FSQA, FSQ1, FSQ2, FSQ4 and FSQ6. These substations provide power to the fishway (lighting, gate controls, portable pumps, heating, and receptacles). To mitigate the arc flash energy at these locations a maintenance switch and indicating light would be installed providing an input to the protective relay associated with the feed to the substation. During maintenance or switching operations the maintenance mode would be used to lower the arc flash incident energy from category 4 to category 1. | Operations or maintenance on these substations could result in an arc flash accident. An arc flash accident with incident energy of category 4 would result in a serious injury or fatality to the personnel involved. The substation equipment would require replacement due to excessive damage and possible fire. If Maintence switches are not installed, personnel will continue to be at an elevated rist of injury. | 4 | 4 | 4 | 4 | 5 |  | 4 | 4.1667
John Day | Submerged Traveling Screen (STS) Rehab | Submerged Traveling Screen (STS) need major overhaul (corrosion, bearings, etc.). There are 48 working screens plus one extra screen (49 total). | All 49 STSs are overdue for refurbishment. Failure to address the issues could result in significant negative impacts to hydropower production at John Day since turbines can not operate without STS's during the fish passage season (April 1st through December 15th). OPperating turbines without STSs is a violation of the Fish Passage Plan and FCRPS BiOp. | 4 | 3 | 4 | 3 | 5 |  | 3 | 3.6667
John Day | JBS Expansion Joint | Needs to be re-designed for the larger/wider cover plates/ recessed wall to stop water leaks | If the joint fails, the JBS is OOS until repairs can be made. This will result in failure to meet BiOp requirements for safe passage for downstream migrants. | 4 | 4 | 4 | 5 | 4 |  | 4 | 4.1667
Bonneville | Bradford Island Fish Ladder Exit | Bradford Island Fishladder Exit requires expensive O&M dredging. A newly designed and built exit channel would remove the need for maintenance dredging in the future | Repeated bi-annual dredging ($250K every 2 years) is required to keep fish ladder exit area deep enough for adult fish passage. | 3 | 5 | 4 | 4 | 4 |  | 4 | 4
The Dalles | Fishway Diffuser | Removal of east fishway collection channel unused diffuser valves and permanent closure. Possible removal of east entrance, junction pool, east lower ladder and north ladder diffuser valves and maintain permanently opened. | The Dalles east fishway passes approximately 80% all Columbia river migrating fish, including 7 ESA listed species. Operation of the east fishway auxiliary water system has changed since original design, with the latest fish passage radiotelemtry information. Collection channel valves are always closed due to this changed operation. Maintenance is unnecessary if not used. Permanent closure method is required due to the degraded state of many of these valves. Failure of unused diffuser valves can result in blown diffuser grating resulting in catastrophic fish kill of ESA listed species. | 2 | 4 | 3 | 3 | 3 |  | 3 | 3
The Dalles | O&M TD Major Rehab Report |  |  | 4 | 4 |  | 3 | 4 |  |  | 2.5
Bonneville | Fish Ladders, Cascades Island Fishway Report - Phase 2 | Diffuser structural problems and air entrainment by fish valves that causes gas supersaturation of fishway above TDG limits (Fish Valve 1-1, 4-3, 4-4, 5-3, 5-4) | We will be unable to meet the BiOp and Fish Passage Plan requirements for passage of the thirteen ESA listed species and all other migrating fish if failure continues at current rate. | 1 | 3 | 3 | 1 | 5 |  | 2 | 2.5
John Day | North Ladder Elevator | The elevator provides safe access and egress for biologists and researchers. | Failure of the elevator puts humans and fish at risk. If the elevator is not working, personnel have to walk up about 12 flights of stairs with a fish bag with fish and water. | 3 | 1 | 3 | 3 | 2 |  | 2 | 2.3333
Bonneville | Spillway Fish Elevators | Fish elevators are non-functional, have not been used in at least 50 years, and are an environmental and safety hazard. Fish elevators need to be decommissioned and removed from the project. The existing areas should be cleaned up and be made available for other uses. | Environmental issues due to potential oil spillage. May have wooden bulkheads that could fail. | 1 | 1 | 1 | 2 | 1 |  | 1 | 1.1667
All ranking is 1-5, similar to SCT.
1 = lowest 5 = highest priority
indicates "defer to Corps"

## COMBO
Project | Location | Work Item | Comment - Red highlighted items currently affect meeting FPP criteria | NWW/NWP | NOAA | USFWS | CRITFC | WDFW | ODFW | IDFG | Average
L Monumental | Spillway | Spillbay 3 | Bay 3 currently tagged OOS due to failed test. | 5 | 5 | 5 | 5 | 5 |  | 5 | 5
McNary | Oregon Fishway | Repair/replace three south shore AWS pumps. | Condition of pumps results in being off line often for repairs. Pumps 1 & 3 currently OOS requiring closing of some entrances to maintain passage criteia | 5 | 5 | 5 | 5 | 5 |  | 5 | 5
John Day | AWS Rehab Remaining 2 Fish Unit Turbine Pumps (SAP Name: Fish HYD Pumps U1 & U2 Rehabilitiation?) | Age of turbines and possibility of failure leads to requirement for rehab. All 3 installed at same time, one has failed and pump 2 is near failure. One remaining functional pump will likely fail soon. | Critical to the Fish Passage Plan and keep John Day within adult passage criteria under the FCRPS BiOp to provide safe passage for Esa listed fish and resident fish species. The units are more than 50 years old and are currently showing major wear with leaking gearbox seals and worn guide bearings. | 4 | 5 | 5 | 5 | 5 |  | 5 | 4.8333
L Goose | Forebay | Repair debris boom | Ineffective design collects debris and allows debris to reach powerhouse where it increases risk of injury and mortality for juvenile fish | 5 | 5 | 4 | 5 | 5 |  | 4 | 4.6667
McNary | Spillway | Rehabe/replace spillway cranes and hoists 6&7 | Cranes and hoists 6&7 underrated for lifting requirements and often OOS for repairs because of age and condition | 5 | 4 | 4 | 5 | 5 |  | 5 | 4.6667
All | Bypass system | Critical spare parts | Lack of sufficient spare parts required juvenile passage to be in emergency bypass March 2021 | 4 | 5 | 4 | 4 | 5 |  | 5 | 4.5
McNary | Spillway | Add hoists to spillbays 2 and 19 | Spillbays 2 and 19 do not contain hoists and can only be operated using two spillway cranes. | 5 | 3 | 4 | 5 | 5 |  | 5 | 4.5
All | Fishways | Support for fishway temperature monitoring | CRIFM funds were provided for installation of temperature sensors that provide real-time posting of fishway temperatures but no funding has been identified for continued O&M. | 4 | 4 | 5 | 4 | 4 |  | 5 | 4.3333
Ice Harbor | Powerhouse deck | Repair/replace trash rake | Failed inspection spring 2021 | 5 | 5 | 4 | 4 | 4 |  | 5 | 4.5
L Monumental | Fishway | Fishway cooling system | Analysis shows potential to cool fishways 1-4 degrees F during warm water periods using structures similar to those installed at Little Goose and Lower Granite dams | 4 | 5 | 5 | 4 | 3 |  | 5 | 4.3333
Lower Granite | Fishway | Rehad/replace fishway AWS pumps | Age and condition of pumps create high risk of failure. | 4 | 4 | 4 | 4 | 4 |  | 5 | 4.1667
John Day | Bonneville Hatchery Well Field | Hatchery well field has iron bacteria problem and local well gravel pack silting. | Critical - loss of fish production, failure to meet John Day Mitigation obligations | 5 | 3 | 5 | 5 | 5 |  | 2 | 4.1667
The Dalles | Fishway Automation | Critical components are past useful life and unsupported by OEM. Originally installed fiber optic cable is failing. Replacement parts are no longer available for purchase. Procure and install new fishway automation for all entrance and exit weirs. | This fishway passes approx 80% of total adult fish passage upstream on the Columbia River. If water levels in the fishladder cannot be regulated then fish passage will be negatively impacted. Seven ESA listed salmonid species pass through this system. | 4 | 4 | 4 | 4 | 4 |  | 5 | 4.1667
The Dalles | Fishway Arc Flash Mitigation | Several pieces of equipment have high arc flash incident energies (Cat 4). Arc Flash Hazard Analysis completed in March 2015 by HDR identified several pieces of equipment with high arc flash incident energies. The analysis provided recommended mitigation to lower the arc flash incident energy to a safe level for personnel. The majority of the recommended mitigation is being completed under a power funded contract; however, there is equipment remaining that requires mitigation which can not be power funded. The equipment with high arc flash incident energies are at substations FSQA, FSQ1, FSQ2, FSQ4 and FSQ6. These substations provide power to the fishway (lighting, gate controls, portable pumps, heating, and receptacles). To mitigate the arc flash energy at these locations a maintenance switch and indicating light would be installed providing an input to the protective relay associated with the feed to the substation. During maintenance or switching operations the maintenance mode would be used to lower the arc flash incident energy from category 4 to category 1. | Operations or maintenance on these substations could result in an arc flash accident. An arc flash accident with incident energy of category 4 would result in a serious injury or fatality to the personnel involved. The substation equipment would require replacement due to excessive damage and possible fire. If Maintence switches are not installed, personnel will continue to be at an elevated rist of injury. | 4 | 4 | 4 | 4 | 4 |  | 4 | 4
Lower Granite | Fishway | Modify adult trap turnpool gate | Convert to lift gate to allow fish to pass upstream without transiting the adult trap at night and weekends during passage season | 4 | 5 | 3 | 4 | 4 |  | 4 | 4
Ice Harbor | South fishway | AWS pump rehab | Aging pumps have high risk of failure | 3 | 4 | 4 | 4 | 4 |  | 4 | 3.8333
L Goose | North shore | Replace north shore jetty | Lost during high flows, protects north shore fishway entrance from shore eddy | 3 | 5 | 3 | 4 | 3 |  | 5 | 3.8333
L Goose | Fishway | Replace fishway control system | Fishway entrances operate in manual mode only, requiring regular inspections and manual adjustments to maintain fishway criteria | 4 | 4 | 5 | 3 | 3 |  | 4 | 3.8333
Lower Granite | Fishways | Rehad/replace fishway entrances. NSE1 and NSE2 are showing cracks in the concrete | Age and condition of fishway entrances create relatively high risk for failure | 4 | 4 | 4 | 3 | 4 |  | 4 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Replace transverse stoplog guides. | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all transverse stoplogs. | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; replace rotovalves, slide gates | Project cannot currently dewater south shore fishway to affect repairs. See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | Oregon Fishway | Rejuvenate dewatering system; Rehabilitate all floating weirs and guides | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 4 | 4 | 4 | 4 |  | 3 | 3.8333
McNary | JFF | Add tailrace bird wires |  | 4 | 5 | 4 | 5 | 5 * |  | 5 | 3.8333
McNary | Oregon Fishway | Replace diffuser gratings and grate supports | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 4 | 5 | 4 | 3 | 4 |  | 3 | 3.8333
Ice Harbor | Fishways | Entrance hoists and controls replacement | Hoists have failed causing fishway to be temporarily closed and out of criteria | 3 | 4 | 5 | 3 | 3 |  | 4 | 3.6667
Lower Granite | Barges | Improve degassing system on 2000 barges | Current pumping system is inadequate to degass river water during periods of high TDG | 4 | 5 | 4 | 3 | 5 |  | 1 | 3.6667
John Day | Submerged Traveling Screen (STS) Rehab | Submerged Traveling Screen (STS) need major overhaul (corrosion, bearings, etc.). There are 48 working screens plus one extra screen (49 total). | All 49 STSs are overdue for refurbishment. Failure to address the issues could result in significant negative impacts to hydropower production at John Day since turbines can not operate without STS's during the fish passage season (April 1st through December 15th). OPperating turbines without STSs is a violation of the Fish Passage Plan and FCRPS BiOp. | 4 | 3 | 4 | 3 | 5 |  | 3 | 3.6667
L Monumental | Forebay | Install shear boom to move debris to spillway | Debris can enter juvenile bypass system, risking injury and mortality to juvenile salmonids | 3 | 5 | 4 | 3 | 3 |  | 3 | 3.5
Lower Granite | Fishway | Correct Control System Programing malfunction | Control system is not accurate, requiring regular inspections and manual adjustments to maintain fishway criteria | 4 | 3 | 5 | 3 | 3 |  | 3 | 3.5
John Day | JBS Expansion Joint | Needs to be re-designed for the larger/wider cover plates/ recessed wall to stop water leaks | If the joint fails, the JBS is OOS until repairs can be made. This will result in failure to meet BiOp requirements for safe passage for downstream migrants. | 4 | 4 | 4 | 5 | 4 |  | 4 | 4.1667
L Monumental | JFF | Hoist system for tailrace tail screens | Current system is insufficient and unsafe to operate | 3 | 3 | 4 | 3 | 4 |  | 3 | 3.3333
Bonneville | Bradford Island Fish Ladder Exit | Bradford Island Fishladder Exit requires expensive O&M dredging. A newly designed and built exit channel would remove the need for maintenance dredging in the future | Repeated bi-annual dredging ($250K every 2 years) is required to keep fish ladder exit area deep enough for adult fish passage. | 3 | 5 | 4 | 4 | 4 |  | 4 | 4
L Goose | Fishway | Re-design fish count station | Turbulence interferes with accurate fish counting | 4 | 2 | 4 | 3 | 4 |  | 2 | 3.1667
L Monumental | JFF | Primary Dewaterer repairs | Worn brass nuts, missing motor, weir held in place with chain | 3 | 3 | 4 | 3 | 3 |  | 3 | 3.1667
McNary | JFF | Replace outfall sprinklers | Sprinklers and supply line lost during high flows in 2018 | 3 | 4 | 4 | 1 | 2 |  | 4 | 3
Ice Harbor | Forebay | Ladder exit debris booms | Current log booms are old and are prone to failure with east winds | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
Ice Harbor | Juvenile fish channel | Expansion of air burst cleaning system under inclined screen | Material purchase needed to keep screens clear of debris | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
L Goose | Fishway | Replace diffuser grating and support beams |  | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
L Goose | Collection channel | Repair/replace corroded outer steel orifice pipe with stainless steal | Orifices have failed mid-season causing them to be closed until winter maintenance period | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
L Goose | Collection channel | Repair orifice valve cylinders |  | 3 | 3 | 2 | 3 | 3 |  | 3 | 2.8333
L Monumental | Fishway | Repair /replace expansion joint seals | Leaks from fishway create saftey risks, particularily during cold weather when ice forms on walkways | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
Lower Granite | Fishway | Install/replace velocity meter in channel | Current system not working, provides inaccurate readings | 3 | 3 | 3 | 3 | 3 |  | 2 | 2.8333
Lower Granite | Fishway | Shad exclusion/ deterrent devise | Reduce adult shad in adult trap and fishway to reduce stress and crowding to salmon migrants, reduce risk from dead shad collecting on gates and screens and potentially reduce shad population upstream of Lower Granite Dam | 3 | 3 | 2 | 3 | 3 |  | 3 | 2.8333
L Goose | Fishway | Repair /replace expansion joint seals | Leaks from fishway create saftey risks, particularily during cold weather when ice forms on walkways | 3 | 3 | 3 | 2 | 3 |  | 2 | 2.6667
The Dalles | Fishway Diffuser | Removal of east fishway collection channel unused diffuser valves and permanent closure. Possible removal of east entrance, junction pool, east lower ladder and north ladder diffuser valves and maintain permanently opened. | The Dalles east fishway passes approximately 80% all Columbia river migrating fish, including 7 ESA listed species. Operation of the east fishway auxiliary water system has changed since original design, with the latest fish passage radiotelemtry information. Collection channel valves are always closed due to this changed operation. Maintenance is unnecessary if not used. Permanent closure method is required due to the degraded state of many of these valves. Failure of unused diffuser valves can result in blown diffuser grating resulting in catastrophic fish kill of ESA listed species. | 2 | 4 | 3 | 3 | 3 |  | 3 | 3
Ice Harbor | Fish count station | Air motors for window brushes | $2500 per motor | 3 | 3 | 3 | 2 | 3 |  | 1 | 2.5
McNary | Oregon Fishway | Permanently close floating orifice gates not used | See MNA WA&OR_FishLadder_Condition Assessment.pdf | 3 | 2 | 2 | 3 | 3 |  | 2 | 2.5
The Dalles | O&M TD Major Rehab Report |  |  | 4 | 4 |  | 3 | 4 |  |  | 2.5
Bonneville | Fish Ladders, Cascades Island Fishway Report - Phase 2 | Diffuser structural problems and air entrainment by fish valves that causes gas supersaturation of fishway above TDG limits (Fish Valve 1-1, 4-3, 4-4, 5-3, 5-4) | We will be unable to meet the BiOp and Fish Passage Plan requirements for passage of the thirteen ESA listed species and all other migrating fish if failure continues at current rate. | 1 | 3 | 3 | 1 | 3 |  | 2 | 2.1667
Ice Harbor | Fishways | Replace missing/broken depth gauages |  | 2 | 4 | 2 | 2 | 2 |  | 1 | 2.1667
Ice Harbor | Juvenile fish channel | Spare actuator for water regulating weirs |  | 2 | 3 | 2 | 2 | 2 |  | 1 | 2
Lower Granite | JFF | Complete Phase 1a modifications and resolve programing issues. | PDW/JBS | 2 | 2 | 3 | 2 | 2 |  | 1 | 2
Lower Granite | Fishway | Permanently close floating orifice gates not used | Reduce leaking and annual maintenenace of stoplogs | 2 | 2 | 3 | 2 | 2 |  | 1 | 2
John Day | North Ladder Elevator | The elevator provides safe access and egress for biologists and researchers. | Failure of the elevator puts humans and fish at risk. If the elevator is not working, personnel have to walk up about 12 flights of stairs with a fish bag with fish and water. | 3 | 1 | 3 | 3 |  |  | 2 | 2
Lower Granite | Fishway | NSE, SSE, and NPE local depth indication | Current system not working, provides inaccurate readings | 2 | 2 | 2 | 2 | 2 |  | 1 | 1.8333
Lower Granite | Fishway | Relocate south shore tailwater elevation sensor |  | 2 | 2 | 2 | 2 | 2 |  | 1 | 1.8333
Ice Harbor | Fishway | Shad exclusion/deterrent devise | Reduce adult shad passing Ice Harbor Dam, potentially reducing shad population in the Snake River | 1 | 1 | 1 | 3 | 1 |  | 1 | 1.3333
Bonneville | Spillway Fish Elevators | Fish elevators are non-functional, have not been used in at least 50 years, and are an environmental and safety hazard. Fish elevators need to be decommissioned and removed from the project. The existing areas should be cleaned up and be made available for other uses. | Environmental issues due to potential oil spillage. May have wooden bulkheads that could fail. | 1 | 1 | 1 | 2 | 1 |  | 1 | 1.1667