# FPP Change Form

Change Request Number: 12BON010 2.4.2.2. VBS reinstallation

Date:  12 January 2012

Proposed by:  Project Fisheries and FPOM

Location of Change:  BON 2.4.2.2.j

Proposed Change:

j. If STS or VBS damage or plugging is detected, follow procedures in Section 4 Fish Facilities Maintenance.  In the event of overwhelming debris (as defined below) follow the procedures outlined below.  Monitor gatewell drawdown daily.

- TIE Crane in Service

A. VBSs will be cleaned by installing the spare VBS in the back slot, pulling the main VBS up and spray it off with a fire hose, then replace back in slot and pull spare (reverse order).

B. If the VBS drawdown criteria of <1.1’ CANNOT be maintained during the day due to debris, the spare VBS will not be installed in the back slot and the gatewells will not be dipped.  The Project will pull the main screen, spray it off with a fire hose, and then re-install.

C. If the VBS drawdown criteria of <1.5’ over a 12 hour period CANNOT be maintained due to debris, even after performing the above operations, then the STSs will be pulled out until the screen re-installation criteria (see 2.4.2.2.j.3) have been met.

D. Once the screens have been removed, these units should operate only as necessary to maintain TDG levels below dissolved gas cap limits.

- TIE Crane OOS- use gantry crane

A. If the Gantry Crane is used to pull the main VBS, the spare VBS will not be installed in the back slot.

B. If the VBS drawdown criteria of <1.5’ over a 12 hour period CANNOT be maintained due to debris, even after performing the above operations, then the STSs will be pulled out until the screen re-installation criteria (see 2.4.2.2.j.3) have been met.

C. Once the screens have been removed, these units should be operated only as necessary to maintain TDG levels below dissolved gas cap limits.

3. SCREEN RE-INSTALLATION CRITERIA-  Once flows drop below 300 kcfs, and water clarity is 4’ or greater,  the Project will install  STSs to in the highest priority unit available.    When VBS drawdown for that unit remains below 1.1’ for 24 hours, the Project will re-install the remaining STSs. The reinstallation process may occur before or after the above criteria are reached at the discretion of the project biologist followed by a discussion with FPOM.

Reason for Change: FPOM requested criteria for screen re-installation that didn’t rely on the Fish Unit trashracks.

Comments from others: FPOM requests more discussion at the February FPOM.

BON Fisheries- The criteria of 300 kcfs and 4’ water clarity are based on experiences from previous years when STS have been pulled and reinstalled. They represent a best guess set of circumstances for a successful reinstallation based on these anecdotal data.

Record of Final Action: approved at 2/9/12 FPOM meeting.