OFFICIAL COORDINATION REQUEST

FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION DATE- 21 October 2009

PROJECT- Bonneville Lock and Dam

RESPONSE DATE- 27 October 2009

Description of the problem- BON is replacing the PH2 480VAC Station Service Switchgear (2-SQ1, 2-SQ2, and 2-SQ3) in 2010.

2-SQ1 is the southernmost PH2 480VAC Station Service Switchgear on the +28 level.  It provides power to the unwatering pumps, drainage pumps, north HVAC, battery banks, etc.  The work on this switchgear will not impact fish facilities.

2-SQ2 is the center PH2 480VAC Station Service Switchgear on the +28 level.  This one provides 480VAC/Non-pref 120VAC to units 11 through 15.  The power is used for the governor oil pumps, head cover pumps, high lift pump, oil re-circulating pumps, etc.  Work on this switchgear will require priority unit outages during fish passage season.  Those outages may be able to occur in the evening hours and are tentatively scheduled to occur between 01 August and 01 November 2010.

2-SQ3 is the northernmost PH2 480VAC Station Service Switchgear located on the +28 level.  It supplies 480VAC/Non-pref 120VAC to units 16 through Fish Unit 2.   Work on this switchgear will require priority unit and fish unit outages.  For that reason, these outages are scheduled for the 2010/2011 winter maintenance season, when the fish units and the Washington Shore fishway will already be out of service.

Type of outage required-

No fisheries related outage required for 2-SQ1.

2-SQ2 will be replaced in two halves.  Units 11-15 will need to be out of service as work progresses on each half and then all units will need to be out of service when the two halves are put together.  A more detailed explanation of the outage required is provided by the engineer below.

When the contractor replaces one of the three 2-SQ switchgear, he will do so 1/2 section at a time.  The 2-SQ switchgears have Bus #1 on the left, Bus #2 on the right.  The 480V switchgear for the individual units, 2-SU11, 2-SU12, etc. are dual fed from the two buses from 2-SQ2.  Say we are taking out Bus #2 first in 2-SQ2.  We will need an outage to take down each individual unit and jumper Bus #2 to Bus #1 inside the particular 2-SUX while the 2-SQ2 Bus #2 is being taken out and replaced.  We will have to do the same for the same 2-SUX when the 2-SQ2 Bus #1 is being taken out and replaced.  Additionally, once the two halves of the 2-SQ2 Switchgear are powered up, the unit and its 2-SUX Switchgear will have to be cleared out to remove the jumper between the two buses in the 2-SUX gear. This will be true for all five of the units and their 2-SUX Switchgear.

Finally, once a 2-SQX switchgear has its two halves installed, it will have to have its tie breaker in the central part of the switchgear connected from one half of the switchgear to the other half.  Since we do not believe that we want to do this when one of the halves of the 2-SQX Switchgear is hot because of safety concerns, we think we will be taking down all of the units attached to that 2-SQX for the period of time that it takes to make the tie breaker connection.

2-SQ3 will be replaced in much the same manner as 2-SQ2.  Units affected are units 16-18 and the two fish units.

Impact on facility operation- Each unit will be out of service for an hour or so while the switchgear gets replaced and then half of the powerhouse will be out of service for a couple of hours as each half of the switchgear is connected together.   Units at PH2 will be impacted by this work from about August 2010 through February 2011.

2-SQ2 and 2-SQ3 will not be replaced concurrently due to safety concerns and concerns about trying to get all the work completed in the winter maintenance season.

Due to the importance of keeping the fish units operating during fish passage season, 2-SQ3 will be replaced during the 2010/2011 winter maintenance period.

Length of time for repairs-  Replacing 2-SQ2 is proposed to start 01 August 2010 and end in November 2010.  Replacing 2-SQ3 is proposed for the 2010/2011 winter maintenance season, when the Washington Shore fishway will be out of service and the fish units will already be shutdown.

The length of time for each unit to be out of service depends on how long it takes to get clearances applied to the 2-SQ2 main units.  Individual unit shutdowns for each 2-SUX clearance and jumpering events will probably be about an hour; connecting the two halves of 2-SQ2 is estimated to take a couple of hours.

Expected impacts on fish passage- Impacts to fish passage for 2-SQ1 and 2-SQ3 are not expected since those switchgear replacement activities either do not impact fish facilities or will occur during winter maintenance, at a time when the fish facilities will already be out of service.

There may be some fish impacts related to replacing 2-SQ2 however.  Units 11 through 15 will each be out of service for about an hour while each half of the switchgear is replaced.  All five units will be out for about two hours while the two halves are connected.

Unit 11 is not expected to return to service until December 2010, so Unit 12 will be the priority unit.  Having the priority unit out of service during fish passage season is less than ideal, however, if the outage is brief in duration and if it can occur during at night, it is anticipated that impacts to fish will be minimal.  Since the work is scheduled to start in August, flows may be low enough that only a couple of units are operating at PH2 to begin with.  Most juveniles will pass through the spillway instead of the powerhouse.

Adult impacts are expected to be minimal if the outages occur at night since adults tend to pass during daylight hours and the sockeye run should be mostly over by August.

Comments from agencies

NOAA Fisheries- This boils down to a corner collector efficiency issue (and therefore, an August issue).  This is the first I have heard that unit 11 will be down until next December.  This seems to be quite a moving target.  There will be at least two units running in this powerhouse in August given the 30 kcfs powerhouse minimum, and what percentage that is of the river is hard to tell, but it could be significant.  The information provided (the engineer's description notwithstanding) was a bit limited.  It seems odd that there is a four month window for a two to three hour outage.  I also wonder about the prospects for problems that might require a longer than anticipated outage.  Without further discussion, I would have to say that August is out for us.  I recommend planning this action for September or later and then only at night to protect adult passage (as indicated in the request).  Thanks,  Gary

BON Tech Staff- I don’t think starting on the first of September instead of the first of August next year would be a critical issue for the replacement of 2-SQ2.  That would still provide 3 months of time for the contractor to replace the 2-SQ2 Switchgear before the start of the Dec. 1, 2010 IWWP.  That IWWP is scheduled for the 2-SQ3 removal/installation.

Assuming that sequentially replacing the two halves of 2-SQ switchgears turns out to be fully practical--and that is the assumption we have been going with until now--then once the 2nd half of the 2-SQ switchgear is installed, the contractor would have to tie the two halves of the switchgear together.  I am assuming that would entail shutting down all of the generator units that are fed station service from that particular switchgear while the tie breaker is being connected.  That event would take place towards the end of the installation for the switchgear.  In the case of the 2-SQ2 replacement, that would be either in mid or late November--given a Sept. 1, 2010 start date.  I would anticipate that doing the estimated two hour connection of switchgear halves at night would be acceptable to the Contractor, COR, and the Project.

I will talk to Tom Tullai and EC Electric about this Fisheries directive that the start date for 2-SQ2 removal/replacement shall not begin before next Sept. 1st.  --Jon T. (x-4574)

NWP (Dasso)- If EC can not install all of the gear in 3 months, we will need an earlier start.  Mark

Final results- Due to concerns about potential fish impacts when units are out of service in August, the start date for the 2-SQ2 replacement will be September.

Please email or call with questions or concerns.

Thank you,

Tammy

Tammy Mackey

NWP Operations Division Fishery Section

Columbia River Coordination Biologist

541-374-4552 Bonneville Office

503-961-5733 Blackberry

Tammy.m.mackey@usace.army.mil