OFFICIAL COORDINATION REQUEST FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE- 12BON08 Gantry 7 rehab

COORDINATION DATE- 29 March 2012

PROJECT- Bonneville Lock and Dam

RESPONSE DATE- 12 April 2012 (FPOM meeting)

Description of the problem- Some of the coordination detailed in 110425 UPDATED 110413 BON Gantry 7rehab.doc is no longer valid and needs further discussion.

Type of outage required- Depending on how many units are left with screens, there may be up to seven main units out of service until DSM2 is dewatered on 13 November (to facilitate Washington Shore lamprey mods).  After DSM2 is dewatered on 13 November, there may be as few as one main unit (and the fish units due to the lamprey work in Washington Shore) out of service.

With the flows shown in Table 1, it may be feasible to have Unit 11 as the only unit with screens since most of the flow may be captured with PH1 capacity and minimal spill.  Once DSM2 is dewatered, there would be only one unavailable unit and Project capacity would be similar to what it has been in recent years during these months.

Table 1.  High, low and average outflows at Bonneville Dam for August – December from 2007 – 2011.

|  |  | 2011 kcfs/ date | 2010 kcfs/ date | 2009 kcfs/ date | 2008 kcfs/ date | 2007 kcfs/ date |
| --- | --- | --- | --- | --- | --- | --- |
| August | Low | 160.1 29 Aug | 96.6 31 Aug | 93.1 17 Aug | 117.0 17 Aug | 117.1 19 Aug |
|  | High | 242.1 1 Aug | 162.1 5 Aug | 159.6 1 Aug | 161.3 7 Aug | 194.7 2 Aug |
|  | Average | 195.3 | 124.5 | 118.1 | 134.6 | 144.6 |
| September | Low | 97.6 24 Sep | 72.7 12 Sep | 71.1 8 Sep | 72.2 21 Sep | 72.2 30 Sep |
|  | High | 156.1 1 Sep | 110.7 30 Sep | 104.2 25 Sep | 118.7 5 Sep | 125.4 1 Sep |
|  | Average | 119.8 | 89.8 | 84.1 | 93.9 | 90.7 |
| October | Low | 88.7 2 Oct | 80.7 4 Oct | 74.4 23 Oct | 74.1 4 Oct | 72 1 Oct |
|  | High | 145.3 15 Oct | 126.4 14 Oct | 119.0 28 Oct | 131.3 15 Oct | 137 18 Oct |
|  | Average | 117.8 | 104.4 | 92.4 | 97.2 | 97.6 |
| November | Low | 121.4 27 Nov | 113.0 7 Nov | 95.1 1 Nov | 81.7 2 Nov | 80.5 4 Nov |
|  | High | 146.5 16 Nov | 149.4 30 Nov | 138.0 9 Nov | 165.0 14 Nov | 131.6 30 Nov |
|  | Average | 133.2 | 125.5 | 119.4 | 121.5 | 115.9 |
| December | Low | 128.1 2 Dec | 122.0 26 Dec | 111.3 21 Dec | 113.8 13 Dec | NA |
|  | High | 165.5 30 Dec | 204.0 15 Dec | 149.1 7 Dec | 162.6 20 Dec | NA |
|  | Average | 139.8 | 145.5 | 131.7 | 132.0 | NA |

Miscellaneous flow tends to be about 12.4 kcfs during fish passage season.  See Table 2 for more information.

Table 2.  BON Miscellaneous flow calculator.

| MISC FLOW CALCULATOR |  |  |
| --- | --- | --- |
| OREGON SHORE | FLOW | SELECT |
| 'A' BRANCH | 2.6 | X |
| 'B' BRANCH | 0.9 | X |
| NAVIGATION LOCK | 0.4 | X |
| PH1 SLUICEWAY | 1.1 | X |
| CASCADE ISLAND |  |  |
| FISH LADDER EXIT OPEN | 1.0 |  |
| FISH LADDER EXIT CLOSED | 0.5 | X |
| WASHINGTON SHORE |  |  |
| FISH LADDER | 0.8 | X |
| UMT | 0.7 | X |
| CORNER COLLECTOR | 5.0 | X |
| DSM2 | 0.4 | X |
| TOTAL MISC FLOW | 12.4 |  |

PH1 capacity, with 10 units available, ranges between 80 – 120 kcfs.  This is dependent on head and location within the 1% band.

PH2 capacity, with 1 unit available, ranges between 10 – 16 kcfs.  This is dependent on head and location within the 1% band.

Summer spill is 75kcfs day/gas cap night.  The gas cap varies depending on tailwater and weather conditions.

Rose highlighted areas on the table reflect flows that could be captured by the middle of the PH1 and one unit at PH2 range and misc. flow.  Equals roughly 114kcfs.

Red highlighted areas on the table reflect flows that could be captured by the high end of the PH1 and one unit at PH2 range and misc. flow.  Equals roughly 148kcfs.

Blue highlighted areas on the table reflect flows that could be captured with summer spill, low to mid- range PH1 capacity, and misc. flows. Equals roughly 167 – 177kcfs.

Impact on facility operation- Without Gantry 7, the Project no ability to pull STSs, or clean VBSs (in the event the TIE crane is restricted by wind).   A barge crane may be situated in the forebay to handle trashrack debris.

The Project cannot pull STSs with the TIE crane and BPA has expressed concern with having up to three units unavailable during the winter months.  An alternative to three units’ worth of STSs may be to install screens in one unit.  This would provide a bit of flexibility to accommodate flows from August to November but only reduce Project capacity to what it has been in the years Unit 11 was out of service.  This option relies on all unscreened units being available for use.  It also reduces the flexibility of splitting powerhouse flows if fish numbers require it, as per the 2012 FPP.

Dates of impacts/repairs- The outage will occur August 2012 through mid- February 2013.

Length of time for repairs- 7 months.

Expected impacts on fish passage- There are likely to be impacts to fish.  Those impacts will be mitigated to the extent possible.  Below are descriptions of the anticipated impacts to fish through 15 December, which is the date the FPP allows for pulling fish screens and dewatering juvenile bypass facilities.  Fish screens are only installed at BON PH2.

Juvenile downstream migrating salmonids- Juvenile salmonids- In August, the bulk of the migrating salmonids are expected to pass via the spillway.  DSM2 is scheduled to be dewatered on 13 November to facilitate Washington Shore lamprey mods.

From September to 12 November, with PH1 priority, it is expected that the bulk of juvenile salmonids will  pass through the ITS or the MGR units at PH1.  Those fish attracted to PH2 would be bypassed through a screened unit, into DSM2 or they would pass through the B2CC.

From 13 November through 15 December, there are expected to be relatively few juveniles migrating.  Those that are migrating would pass primarily through the ITS or MGRs are PH1 and through unscreened units at PH2.

Adult downstream migrating salmonids- Adults moving downstream will not have the protection provided by screened units at PH2, however, from August to October, the bulk of the river may be spilled (August only) or passed through PH1.  The ITS at PH1 will provide a safe surface passage route for adults.  From November through 15 December, PH1 will remain the priority powerhouse, however, any fish passing through PH2 will go through an unscreened turbine.

Adult upstream migrating salmonids- The August – February Gantry crane outage is concurrent with fall Chinook, fall coho, and steelhead runs.  Adult salmon and steelhead fallback via the spillway is a primary concern for the Region, as several radio-telemetry studies have suggested a positive correlation between spill and fallback of Bradford Island Fish Ladder-passed salmon and steelhead.  Furthermore, these studies indicated that fish that fallback at any monitored dam had a negative effect on escapement.  Spill volume is a factor in fallback of Bradford Island-passed fish, so the 2012 FOP specifically limits BON daytime spill from June 16 through August spill to 100 kcfs or less.  The FOP also indicates that the daytime spill amount shall be 75 kcfs from August 1-31 to accommodate juvenile salmon passage.  This is the greatest period of risk to adult migrants, as the juvenile salmon passage season ends August 31.  From September 1 – February 28, except in forced-spill conditions, spill will only occur at Spillbays 1 and 18 in the form of attraction flow for Cascades Island and B- Branch fish ladders.

Pacific Lamprey - The August – February gantry crane outage concurrent with the later component of the adult Pacific lamprey run.  Overall lamprey passage efficiency of the Bradford Island Fish Ladder is superior to that of the Washington Shore fishway, so there may be some passage benefit associated with a PH1 priority operation.  As with adult salmonids, the greatest fallback risk for lamprey occurs during the higher spill conditions of August 1-31.

Comments from agencies

NWP BON Tech Staff-----Original Message-----
From: Perletti, Kevin P NWP 
Sent: Friday, March 30, 2012 7:46 AM
Subject: RE: DRAFT MOC 12BON08 Gantry 7 rehab

The "barge crane" you mention as being in the forebay to handle trash debris is not a contract requirement. Rather the PM has stated he would financially support an "emergency contract" if needed at the time to handle trash. This decision would obviously be subject to available funding as an emergency barge crane at that time may be very expensive. As far as this same crane performing trash racking at the FUs, I do not think that would be feasible. I think realistically a barge crane can only perform clamshell trash handling. Kevin P. Perletti P.E.

NWP BON Maintenance-----Original Message-----
From: Kirk, Tony R NWP 
Sent: Thursday, March 29, 2012 4:31 PM
Subject: RE: DRAFT MOC 12BON08 Gantry 7 rehab

I like the idea of only installing screens in one unit opposed to the outlined three.  We need to remember that these screens have gearboxes and bladders that contain oil.  If we encounter a failure and leak oil to the slot, there is no way to remove the screen for repairs.  Not only will we lose generation but we increase our chances of an environmental issue.

2012 April 12 FPOM: 12BON08 BON Gantry 7 rehab.  FPOM generally approves, but BPA still needs to give concurrence.  ACTION: Bettin will send an email to Mackey as soon as he gets that.

2012 May 10 FPOM: BPA provided their concurrence.

Final results-

Late July 2012- The Project will move forward with switching powerhouse priority to PH1 and removing screens from all but Unit 11 just prior to Gantry 7 going out of service.  Flow will be contained within PH1, the spillway and Unit 11 from when screens are pulled through 30 August 2012.

September 2012- Flow will be contained within PH1, Unit 11 and spill (if needed) from 1 September through 13 November 2012.  DSM2 will be prepared for dewatering starting on 13 November.

November 2012- Flow will be contained within PH1, Units 12-18 (these are unscreened units) and spill (if needed) from 13 November 2012 through 28 February 2013.

Please note- PH1 and screened units will be operated through 12 November 2012.  As soon as the DSM goes OOS, PH2 unscreened units will be operated.  Screened units may NOT be operated once DSM2 is OOS.

Please email or call with questions or concerns.

Thank you,

Tammy

Tammy Mackey

NWP Operations Division Fishery Section

Columbia River Coordination Biologist

503-961-5733

Tammy.m.mackey@usace.army.mil

Figure 1.  Gantry 7 rehab schedule.