OFFICIAL COORDINATION REQUEST

FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION DATE-  11/5/2008

PROJECT-  John Day Dam

RESPONSE DATE-  As soon as possible.

Description of the problem

JDA Electrical crew is asking for an emergency outage of line 1 to clean cormorant poop from the 500Kv insulators.

They would like to perform this cleaning at 0630 on 15 November.

Type of outage required

The JDA line 1 outage will require Units 1-4 to be out of service.

Impact on facility operation

If this cleaning is not performed there is a high risk of arcing (which happened early this week).  This work needs to be performed before the inclement weather hits.  The Project needs approval as soon as possible to coordinate equipment and people.

Length of time for repairs

A total of four hours is requested.  This includes two hours for cleaning and time to hang and remove the clearance.

Expected impacts on fish passage

The fishway will have reduced attraction flow, but there are few adults passing this time of year so the impacts should be minimal during this outage.

Flushing flow will be reduced for the SMF outfall as well.  Given the time of year, there are very juveniles so there should be minimal impact to them as well.

Comments from agencies

Final results

Please email or call with questions or concerns.

Thank you,

Tammy

Tammy Mackey

NWP Operations Division Fishery Section

Columbia River Coordination Biologist

541-374-4552 Bonneville Office

503-691-5733 Blackberry

Tammy.m.mackey@usace.army.mil