OFFICIAL COORDINATION REQUEST

FOR

NON-ROUTINE OPERATIONS AND MAINTENANCE

COORDINATION TITLE:  12 LMN011 Dive to remove STS screen

COORDINATION DATE-  October 17, 2012

PROJECT- 	Lower Monumental Dam

RESPONSE DATE-   before 10/25

Description of the problem:	  Stuck STS screen in Main Unit 1.  We are sending in divers on 11/6 to fix the issue

About two months ago it was realized that the STS screen in slot B of Main Unit 1 was stuck in the deployed position.  Several efforts have failed to retract the screen.  On 10/17, an ROV inspection revealed that wood debris is lodged between the extendable portion of the screen frame and the concrete wall.  The screen material is intact and the screen is operable.

A dive to remove this debris is scheduled for 11/6.  This dive is a penetration dive with some risk associated with it.  To aid in communication and reduction of vibration and interference, the divers have asked that all adjacent units be out of service for the dive.  This request requires that Main Unit 2 be taken out of service for the Main Unit 1 dive.

Unit 1 is last in Unit priority at this time and the flows are such that we cannot run it.  Unit 2 is first in priority. Lower Monumental will need to deviate from unit priority table in the FPP for this dive.  We are requesting to run Main Unit 4 during the outage.  Main Unit 3, which is second in priority on the table will be out of service at that time for annual maintenance.

Type of outage required:  Main Unit 2 outage for the day of 11/6

Impact on facility operation:

Length of time for repairs:  0700-1700 on 11/6

Expected impacts on fish passage:

Fish runs are very light during this timeframe and the impact of this outage should be minimal for the fish in the river.  Adult fish counting ends October 31.  By this period the bulk of all adult fish runs have past and few fish remain in the system.  The STS screens on non-operating units can be raised after October 1 so long as the unit will not be run without a full complement of STS screens until the end of the juvenile bypass/fallback season December 15. Unit 1 will not be run during this period and the raising of its screens will expedite required maintenance.  All screens will need to be raised shortly after mid December for annual maintenance so the removal of the debris blocking the deploying arm is essential.

Monthly passage at Lower Granite Dam in 2010 for all of November was 668 chinook and 7,620 sheelhead. This 10 hour outage of unit 2 at Lower Monumental with all fishladder criteria maintained will delay few fish.  If the delay of these few fish is problematic then unit 5 or 6 might be operated to draw fish into the south powerhouse entrances during this short time period.

Comments from agencies:

-----Original Message-----
From: Tom Lorz [mailto:lort@critfc.org] 
Sent: Friday, October 19, 2012 2:29 PM
To: Moody, Gregory P NWW
Subject: Re: FPOM: Official Coordination 12 LMN011 Dive to remove stuck STSscreen (UNCLASSIFIED)

don't see a problem with this.

thanks

tom lorz

From: Bill Hevlin [mailto:bill.hevlin@noaa.gov] 
Sent: Tuesday, October 23, 2012 12:31 PM
To: Moody, Gregory P NWW
Cc: Bailey, John C NWW; Setter, Ann L NWW; Fone, Kenneth R NWW; Ritchie Graves; Gary Fredricks; Trevor Conder; Tom Lorz; Kiefer, Russ; Bill Hevlin
Subject: Re: FPOM: Official Coordination 12 LMN011 Dive to remove stuck STS screen (UNCLASSIFIED)

Greg, thank you for the coordination request 12 LMN011 Dive to remove STS screen.

NOAA understands that the Corps needs to remove lodged woody debris that is blocking the removal of the STS screen in slot B of main unit one at Lower Monumental.  The Corps has scheduled divers to remove the debris on November 6, 2012.  Due to the risk associated with the dive, the adjacent unit, #2, must be shut down during the dive that day. Unit two is currently the priority operation unit for adult attraction to the north shore powerhouse ladder entrance.  The Corps proposes to change unit operation priority to unit 4 during the dive on November 6 (unit 3 is currently unavailable).

NOAA agrees with the Corps that the proposed change in unit priority may delay some listed adult salmon from locating the ladder entrance, but the time period of delay will be relatively short and it should not have any lasting impact on migrating adults.  Hence, NOAA has no problem with the shift in unit priority proposed by the Corps.

Bill Hevlin

Senior Fisheries Biologist

NOAA Fisheries

Final results:

Thank you,