## Sheet1
Focus Area | Business Line | Project | Asset(s) Description | Condition | Consequences | Risk | PM or POC | Work Type: Study/ Repairs | Est Cost | Comments
Fish Facilities |  | MCN | Bulkheads for WA Shore adult ladder | F - Failed | I - High |  | Coleman
Fish Facilities |  | MCN | Repair WA Fish Ladder Construction Joints | F - Failed | I - High |  | Coleman |  | 350 K | Repair leaking construction joints in the WA Fish Ladder.
Fish Facilities |  | MCN | trash rake | F - Failed | I - High |  | Coleman
Fish Facilities |  | MCN | Backup fish pump for AUX water supply | F - Failed | I - High |  | Coleman
Fish Facilities |  | MCN | Upgrade Fish Pump House #1 Stop Logs | F - Failed | II - Medium High |  | Coleman |  | 500 K | Upgrade and repair fish pump house #1 stop logs taken out of service in 2009 after structural deficiencies were noted
Fish Facilities |  | MCN | Emergency Turbine Intake Gate Closure | NA | III - Medium |  | Coleman |  | 7.5 M | safety requirement.
Fish Facilities |  | MCN | New VBS Frames | D - Poor | III - Medium |  | Coleman |  | 700 K | 9 VBS frames are distorted and reaching the point of being non functional
Fish Facilities |  | MCN | Repair/Replace Spillway Gates Hoist Systems | C-Marginal | II - Medium High |  | Coleman |  | 3 M | Repair/Replace existing spillway gate hoists which are currently operating in an overload condition. Safety& inability to meet court ordered spill
Fish Facilities |  | MCN | Repair OR Fish Ladder Bulkhead Slots | D - Poor | III - Medium |  | Coleman
Fish Facilities |  | MCN | Repair Fish Facilities Stop Log Lifting Beams | C-Marginal | III - Medium |  | Coleman |  | 200 K
Fish Facilities |  | MCN | Mini-tug for debris removal | NA | III - Medium |  | Coleman |  | 300K
Fish Facilities |  | IHR | Replace south shore collection channel grating | D - Poor | I - High |  | Golladay |  | 450K
Fish Facilities |  | IHR | Replace north shore collection channel grating | D - Poor | I - High |  | Golladay |  | 450K
Fish Facilities |  | IHR | Bulkhead and Lifting beam for South Shore Fish ladder | D - Poor | I - High |  | Golladay |  | 172.5K
Fish Facilities |  | IHR | Fish Ladder Staff Gauges | D - Poor | I - High |  | Golladay |  | 233K
Fish Facilities |  | IHR | Install Anodes on STS's at the project | D - Poor | I - High |  | Golladay |  | 100K
Fish Facilities |  | IHR | North Shore Fish Pump Motor Crane Upgrades | D - Poor | I - High |  | Golladay |  | 80K
Fish Facilities |  | IHR | Fish Pump Motor RTDs | C-Marginal | III - Medium |  | Golladay |  | 115K | South Shore fish pumps have bearing and stator temperature indication
Fish Facilities |  | IHR | Install Redundant Electronic sonar on fishway entrances | C-Marginal | III - Medium |  | Golladay |  | 55K | The current level indication for the fish entrances on the Norht and South Shore are not installed in the appropriate location.
Fish Facilities |  | LGO | ESBS Fish Screen Control Upgrade | C-Marginal | II - Medium High |  | Breiten |  | 116K | Replacing the fish screen position sensors on each fish screen with water proof sensors. Replace existing outdated wiring in each control panel. Upgrade communication and data links to the control room
Fish Facilities |  | LGO | ESBS Rehab | C-Marginal | II - Medium High |  | Breiten |  | 200K
Fish Facilities |  | LGO | Upgrade A and B Side Fish Routing Flumes and Routing Pipes | B - Fair | II - Medium High |  | Breiten |  | 250K | Upgrade A and B Side Fish Routing Flumes and fish routing pipes.
Fish Facilities |  | LGO | New Diffuser Gratings for Adult Fish Channel | C-Marginal | II - Medium High |  | Breiten |  | 600K | Modify sizing at same time to be lamprey compliant
Fish Facilities |  | LGO | Upgrade NSE1 Fishway Entrance Weir Hoist Machinery | F - Failed | II - Medium High |  | Breiten |  | 390K
Fish Facilities |  | LGO | Upgrade NSE2 Fishway Entrance Weir Machinery | F - Failed | II - Medium High |  | Breiten |  | 390K
Fish Facilities |  | LGR | Repair Juvenile Fish Transportation Barges | C-Marginal | II - Medium High |  | Mendiola |  | 5 M | Barges need modernizations and repair of ageing structures
Fish Facilities |  | LGR | Rehab fish screens | C-Marginal | II - Medium High |  | Mendiola |  | 1.5 M | Rehab fish screens to mitigate the effects of surface corrosion.
Fish Facilities |  | LGR | Rehab adult fishway floating orifice gates | C-Marginal | II - Medium High |  | Mendiola |  | 480K | Rehab 10 floating orifice gates. Procure a spare gate so repairs could be made throughout the year.
Fish Facilities |  | LGR | Rehab Adult Fishway Entrance weir gates and hoist. | B - Fair | I - High |  | Mendiola |  | 540 K | Rehab Adult Fishway entrance weir gates and associated hoist mechanism. There are 6 total (NSE 1&2, NPE 1&2,SSE 1,2)
Fish Facilities |  | LGR | new 4000 series barges | NA | III - Medium |  | Mendiola |  | 6 M | alternative to repair above
Fish Facilities |  | LGR | Install new diffuser grating throughout adult fishway | B - Fair | II-Medium High |  | Mendiola |  | 250 K
Fish Facilities |  | LGR | Upgrade Vertical Barrier Screen | B - Fair | III - Medium |  | Mendiola |  | 450 K
Fish Facilities |  | LGR | Fish Screen Control Sys Upgrade | B - Fair | III - Medium |  | Mendiola |  | 166.6 K | Upgrade ESBS Fish Screen control system. Replace e with modern PLC control, and provide operating conditions in control room.
Fish Facilities |  | LGR | FISH BARGE MRG ACCESS PLATFORMS | C - Marginal | III - Medium |  | Mendiola |  | 75K | Design and install access ramp extensions for fish barge access.
Fish Facilities |  | LGR | Upgrade adult trap drain valve sluice gate operator | C - Marginal | II - Medium High |  | Mendiola |  | 41 K
Fish Facilities |  | LGR | Upgrade Adult Fish Counting Station | C - Marginal | II - Medium High |  | Mendiola |  | 75 K
Fish Facilities |  | LGR | Upgrade Fishway controls | C - Marginal | III - Medium |  | Mendiola |  | 320 K
Fish Facilities |  | LGR | Fish Facility - Design and Install New Slide Gates | D - Poor | III - Medium |  | Mendiola |  | 125 K
Fish Facilities |  | LGR | Fishpump motors | C - Marginal | II - Medium High |  | Mendiola |  | 40 K | Procure spare motor, or send existing ones out to be refurbished.
|  | LGR | Fishway Entrances NSE1&NSE2 | F - Failed | I - High |  | Mendiola |  | 800 K | Rehabilitate failed NSE 1 & NSE 2
Fish Facilities |  | LGR | Fishway Entrance Bulkhead NPE3 and NSE3 | D - Poor | II - Medium High |  | Mendiola |  | 560 K | Repair or replace failed NPE3 and NSE3.
Fish Facilities |  | LMN | Replace STS Link Bars | C-Marginal | II - Medium High |  | Witham |  | 450 K | Replace and improve STS Link Bars on all 19 fish screens
Fish Facilities |  | LMN | Comply with Emergency Turbine Intake Gate Closure Requirements | F - Failed | I - High |  | Witham |  | 6.2 M | Implementation of this measure may require the installation of new fixed hoists to operate the intake gates.
Fish Facilities | ENS | LMN | Replace Diffuser Gratings, Supports, Mud Valves and clean supply conduits | C-Marginal | II - Medium High |  | Witham |  | 850 K
Fish Facilities |  | LMN | Replace Fish Pumps 1 & 2 | D - Poor | II - Medium High |  | Witham |  | 575 K | Replace fish pumps #1 and #2 to include replacing the diffuser assembly and bearing housing. Bearing housings have already failed and temp repairs have been made. LMA will be operating outside criteria of fish passage plan if one pump fails.
Fish Facilities |  | LMN | Place Concrete Outrigger Footing at RSW | NA | I - High |  | Witham |  | 116 K | Install concrete outrigger footing at RSW on spillway deck. Current configuration requires operating crane at crane limits (i.e. no safety margin)
Fish Facilities |  | LMN | STS Removable Work Platform | C-Marginal | IV - Low |  | Witham |  | 25 K | Design and Fabricate Removable Work Platform for STS Work in Gate Repair Pit