# FPP Change Request Form

Change Request Number: 14BON001 Table BON-16 Add Mid-Range

Date Submitted:  3/29/2013

Project: BON

Requester Name, Agency: FPOM BON Ops Task Group

Location of Change - FPP Project and Section:

BON sections 5.2 and 5.3 (Turbine Unit Operations and Maintenance), and Table BON-16 (PH2 turbine 1% range)

Proposed Changes:

- 5. Turbine Unit Operation and Maintenance

- 5.1. Powerhouse priority is detailed in Table BON-14.  When splitting flows, as directed in section 2.1.2, the top two available priority units for PH1 will be operated first followed by normal unit priority at PH2.  If there is a need for more units, and all available units at PH2 are in operation, proceed with the normal unit priority for PH1.

5.2. November 1 through March 31.  All turbine units will operate as a soft constraint within ±1% of peak efficiency (within upper and lower limits of the 1% range) as shown in Tables BON-15 (PH1) and BON-16 (PH2) for project heads of 35-70 feet.  See BPA Load Shaping Guidelines (Appendix C) for further information on turbine operations within and outside of the 1% range.

5.3. April 1 through October 31.  Except as defined below in section 5.3.1, all turbine units will operate as a hard constraint within ±1% of peak efficiency (within upper and lower limits of the 1% range) as shown in Tables BON-15 (PH1) and BON-16 (PH2).

5.3.1. April 10 through August 31.  During the spring and summer spill seasons when the project is spilling in accordance with the Fish Operations Plan (FOP, see Appendix E), turbine units will operate in the following priority order to pass increasing flow:

- Operate PH2 units within the 1% mid-range (Table BON-16);

- Then, operate PH1 units up to the 1% upper limit (Table BON-15);

- Then, operate PH1 units up to Best Operating Point (BOP; Table BON-15);

- From April 10 through June 20 (spring spill season), additional flow above what can be passed in steps 1-3 will be passed in one of the two following ways, as directed by Project Fisheries based on monitoring of juvenile and adult spring Chinook passage and collection data:

  - If the adult trigger is met (adult counts exceed juvenile collection counts for two consecutive days), then operate PH2 up to the 1% upper limit in the following unit priority order: 18, 17, 16, 15, 14, 13, 12, 11 until adult counts drop below juvenile counts for 3 consecutive days.

  - If the adult trigger is not met (adult counts are less than juvenile collection counts for two consecutive days), then increase spill to pass the additional flow.

- From June 21 through August 31 (summer spill season), additional flow above what can be passed in steps 1-3 will be passed by operating PH2 up to the 1% upper limit.

5.4. The project turbine unit maintenance schedules will be reviewed by Project and Operations Division biologists for fish impacts.  If possible, maintenance of priority units will be scheduled for winter maintenance periods, or when there are low numbers of fish passing the project.

Existing Language For Section 5:

- 5. Turbine Unit Operation and Maintenance

- 5.1. Powerhouse priority is detailed in Table BON-14.  When splitting flows, as directed in section 2.1.2, the top two available priority units for PH1 will be operated first followed by normal unit priority at PH2.  If there is a need for more units, and all available units at PH2 are in operation, proceed with the normal unit priority for PH1.

5.2. Turbine units at PH1 will operate within 1% of best efficiency and within cavitation limits at various head ranges as shown in Table BON-15.

5.2.1. Turbine units at PH2 will operate at the mid to lower 1% range (unless total dissolved gas waivers are exceeded in the tailrace) of best efficiency and within cavitation limits at various head ranges as shown in Table BON-16.

5.3. Turbines will be operated within ±1% of best turbine efficiency from April 1 through October 31 (as specified in the BPA load shaping guidelines), except as outlined in Appendix C.

- 5.4. The project turbine unit maintenance schedules will be reviewed by Project and Operations Division biologists for fish impacts.  If possible, maintenance of priority units will be scheduled for winter maintenance periods, or when there are low numbers of fish passing the project.

Justification for Change:

FPOM requested adding PH2 1% mid-range columns since PH2 may be limited to mid-range operation.  See Memo to FPOM from Bonneville Turbine task group for justification.

Comments from others: See FPC memo

Record of Final Action:

Table BON-16.  Bonneville Dam Powerhouse Two Turbine Units 11-18 (with and without STSs) Output (MW) and Discharge (cfs) at the Upper, Mid-Range and Lower Limits of the 1% of Peak Efficiency Operating Range.

| Head (feet) | Powerhouse Two (units 11-18) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1% Limits With STS |  |  |  |  |  | 1% Limits Without STS |  |  |  |  |  |
|  | Lower Limit |  | Mid-Range 13K – 15K |  | Upper Limit |  | Lower Limit |  | Mid-Range |  | Upper Limit |  |
|  | (MW) | (cfs) | (MW) | (MW) | (MW) | (cfs) | (MW) | (cfs) | (MW) | (cfs) | (MW) | (cfs) |
| 35 | 27.6 | 11,259 | 31.9 | 36.8 | 44.3 | 18,068 | 28.2 | 11,444 | 36.7 | 14,861 | 45.1 | 18,277 |
| 36 | 28.5 | 11,271 | 32.9 | 37.9 | 45.8 | 18,097 | 29.2 | 11,455 | 37.9 | 14,881 | 46.6 | 18,306 |
| 37 | 29.4 | 11,279 | 33.9 | 39.1 | 47.3 | 18,121 | 30.1 | 11,464 | 39.1 | 14,898 | 48.1 | 18,331 |
| 38 | 30.3 | 11,284 | 34.9 | 40.3 | 48.8 | 18,139 | 31.0 | 11,470 | 40.4 | 14,910 | 49.7 | 18,350 |
| 39 | 31.3 | 11,287 | 36.0 | 41.6 | 50.3 | 18,153 | 32.0 | 11,473 | 41.6 | 14,919 | 51.2 | 18,364 |
| 40 | 32.2 | 11,288 | 37.1 | 42.8 | 51.8 | 18,162 | 32.9 | 11,474 | 42.8 | 14,924 | 52.7 | 18,374 |
| 41 | 33.0 | 11,259 | 38.1 | 44.0 | 53.3 | 18,197 | 33.7 | 11,445 | 44.0 | 14,927 | 54.3 | 18,409 |
| 42 | 33.8 | 11,230 | 39.1 | 45.2 | 54.9 | 18,228 | 34.6 | 11,415 | 45.2 | 14,928 | 55.8 | 18,441 |
| 43 | 34.6 | 11,201 | 40.2 | 46.3 | 56.4 | 18,255 | 35.4 | 11,386 | 46.4 | 14,927 | 57.4 | 18,468 |
| 44 | 35.4 | 11,172 | 41.2 | 47.5 | 57.9 | 18,278 | 36.2 | 11,357 | 47.6 | 14,925 | 58.9 | 18,493 |
| 45 | 36.2 | 11,144 | 42.2 | 48.7 | 59.4 | 18,299 | 37.0 | 11,328 | 48.8 | 14,921 | 60.5 | 18,514 |
| 46 | 37.0 | 11,139 | 43.2 | 49.8 | 61.0 | 18,366 | 37.9 | 11,324 | 50.0 | 14,953 | 62.1 | 18,581 |
| 47 | 37.8 | 11,135 | 44.2 | 51.0 | 61.9 | 18,200 | 38.7 | 11,319 | 50.9 | 14,867 | 63.0 | 18,415 |
| 48 | 38.7 | 11,129 | 45.2 | 52.1 | 62.7 | 18,040 | 39.6 | 11,314 | 51.7 | 14,785 | 63.8 | 18,255 |
| 49 | 39.5 | 11,124 | 46.2 | 53.3 | 63.5 | 17,887 | 40.4 | 11,308 | 52.6 | 14,705 | 64.7 | 18,101 |
| 50 | 40.3 | 11,118 | 47.2 | 54.4 | 67.5 | 18,598 | 41.3 | 11,303 | 55.0 | 15,060 | 68.7 | 18,817 |
| 51 | 41.3 | 11,154 | 48.1 | 55.5 | 69.8 | 18,850 | 42.2 | 11,339 | 56.7 | 15,206 | 71.1 | 19,072 |
| 52 | 42.3 | 11,187 | 49.1 | 56.7 | 72.1 | 19,091 | 43.2 | 11,373 | 58.3 | 15,345 | 73.4 | 19,316 |
| 53 | 43.2 | 11,219 | 50.1 | 57.8 | 74.5 | 19,323 | 44.2 | 11,405 | 60.0 | 15,478 | 75.8 | 19,551 |
| 54 | 44.2 | 11,249 | 51.0 | 58.8 | 76.5 | 19,536 | 45.2 | 11,436 | 60.9 | 15,434 | 76.5 | 19,431 |
| 55 | 45.2 | 11,278 | 52.1 | 60.1 | 76.5 | 19,115 | 46.2 | 11,466 | 61.4 | 15,221 | 76.5 | 18,975 |
| 56 | 46.4 | 11,343 | 53.2 | 61.3 | 76.5 | 18,718 | 47.4 | 11,531 | 62.0 | 15,056 | 76.5 | 18,581 |
| 57 | 47.6 | 11,404 | 54.2 | 62.6 | 76.5 | 18,336 | 48.6 | 11,593 | 62.6 | 14,898 | 76.5 | 18,202 |
| 58 | 48.8 | 11,461 | 55.4 | 63.9 | 76.5 | 17,967 | 49.9 | 11,652 | 63.2 | 14,744 | 76.5 | 17,836 |
| 59 | 50.0 | 11,515 | 56.5 | 65.1 | 76.5 | 17,611 | 51.1 | 11,707 | 63.8 | 14,595 | 76.5 | 17,483 |
| 60 | 51.2 | 11,567 | 57.6 | 66.4 | 76.5 | 17,267 | 52.3 | 11,760 | 64.4 | 14,451 | 76.5 | 17,142 |
| 61 | 51.8 | 11,532 | 58.5 | 67.5 | 76.5 | 16,978 | 53.0 | 11,724 | 64.8 | 14,291 | 76.5 | 16,857 |
| 62 | 52.5 | 11,498 | 59.5 | 68.6 | 76.5 | 16,699 | 53.7 | 11,690 | 65.1 | 14,136 | 76.5 | 16,582 |
| 63 | 53.1 | 11,466 | 60.4 | 69.7 | 76.5 | 16,428 | 54.3 | 11,657 | 65.4 | 13,986 | 76.5 | 16,315 |
| 64 | 53.7 | 11,434 | 61.3 | 70.7 | 76.5 | 16,166 | 55.0 | 11,625 | 65.8 | 13,841 | 76.5 | 16,056 |
| 65 | 54.4 | 11,405 | 62.3 | 71.8 | 76.5 | 15,912 | 55.6 | 11,595 | 66.1 | 13,701 | 76.5 | 15,806 |
| 66 | 55.4 | 11,448 | 63.2 | 72.9 | 76.5 | 15,671 | 56.7 | 11,639 | 66.6 | 13,605 | 76.5 | 15,570 |
| 67 | 56.5 | 11,490 | 64.2 | 74.0 | 76.5 | 15,437 | 57.8 | 11,682 | 67.2 | 13,512 | 76.5 | 15,341 |
| 68 | 57.5 | 11,532 | 65.1 | 75.1 | 76.5 | 15,210 | 58.9 | 11,724 | 67.7 | 13,422 | 76.5 | 15,119 |
| 69 | 58.6 | 11,571 | 66.1 | 76.3 | 76.5 | 14,990 | 59.9 | 11,764 | 68.2 | 13,334 | 76.5 | 14,903 |
| 70 | 59.6 | 11,610 | 67.0 | 77.3 | 76.5 | 14,775 | 61.0 | 11,803 | 68.8 | 13,248 | 76.5 | 14,693 |

*  Table based on data provided by HDC, January 2001 (Table BON-16 revised 2006).