From: Bettin,Scott W (BPA) - KEWR-4 [mailto:swbettin@bpa.gov] 
Sent: Thursday, December 20, 2012 12:03 PM
Subject: Generation restrictions at BON

FPOM:

Below is a copy of the schedulers log covering the generation capabilities for the BON 115kv and 230kv transmission lines. These restrictions were put in place to comply with current WECC standards. The values change by season due to changes in air temperature.  We took these limitations and went back and compared them to generation over the last two high flow years.  The outcome of the comparison was that it changed the powerhouse capacity from 0-15 kcfs through the four powerhouse units on the 115 kv system.  Model runs have shown that this limitation is most restrictive in March when the tailwater is low and the head is the greatest.  The second table is the conversion of megawatts to flow (using an average h/k of 4.2) and it shows the amount of water that can pass through the powerhouse by season.

| BON SOC 837723 839321 839323 | Begins: Sep 27 2012 Ends: May 31 2013 START DATE/TIME. June 01, 2012 at 0000 hours Continuous to. END DATE/TIME:. May 31, 2013 at 2400 hours. REASON FOR NOTIFICATION. Transmission System Conditions are cause for this limitation. GENERATION CONSIDERATION. Maximum allowable 230 kV generation at North Bonneville (seasonal limits): June 1 - September 30 at 2400: 690 mw October 1 at 0000 - 31 at 2400: 816 mw November 1 at 0000 - March 15 at 2400: 978 mw March 16 at 0000-May 31 at 2400: 816 mw. DART Form No.. 837723, 839321, 839323, 839325. ORIGINATOR. Ronald H Sevier. |
| --- | --- |

Conversion of megawatts to flow with the current limits:

|  |  | 115 kV Generation Limit | 230 kV Generation Limit | Max turbine capacity | Misc. Flow | Total max flow w/o spill |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | MW | MW | kcfs | kcfs | kcfs |  |
|  | Jun 1 – Sep 30 | 150 | 690 | 195.3 | 6.9 -11.6* | 206.9 |  |
|  | Oct 1 – Oct 31 | 160 | 816 | 227.0 | 6.9 | 233.9 |  |
|  | Nov 1 – Mar 15 | 185 | 978 | 270.5 | 9 | 279.5 |  |
|  | Mar 16 – May 31 | 160 | 816 | 227.0 | 6.9-11.6* | 238.6 |  |
|  | * The corner collector ( 5 kcfs) is shown in Misc. flow |  |  |  |  |  |  |