PH2 UNIT SLOW ROLL

1. Move blades to steep at governor cab by slowly pulling up knob on cam and slowly lowering knob.

2. Put lead turbine bearing oil pump in run.

3. 43 switch to Local.

4. Thrust bearing oil pump to auto – make sure light is lit.

5. Brakes off.

6. Gate lock to off and hold while moving gates.  You can probably release switch when thrust pump light goes out.

7. Raise gate limit slowly. Slowly increase rpm’s for 10 minutes.

8. 43 switch back to central.

9. Thrust pump in auto.

10. Brakes in auto.

11. Lead turbine bearing pump to auto.

To slow roll from governor cabinet do steps 1-5 and then close valves 2 and 4 in cabinet. Open valve 3.

Move gate limit until flow is heard. Slowly roll unit to full rpm’s over 10 minutes. At 40 rpm’s, you can reposition valves 3, 2 and 4 and put turbine bearing pump in auto. At full rpm’s you can do steps 8, 9 and 10.