### CENWP-OP-B                                                                                                      28 March 2000

MEMORANDUM FOR CENWP-OP, ATTN:  Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 12 of 2000, which covers the period 19 through 25 March.

- OPERATION SUMMARY.

1.1. Daily average river flow ranged from 173.9 to 212.2 kcfs.  Daily average tailwater elevation for the project ranged from 15.8’ to 17.8’ msl.  River temperature ranged from 45 to 46° F.  Spill bays 1 and 18, which supply attraction flow for the Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

- First powerhouse unit 10 remained out of service for stator rewind, and unit 18 remained out of service for stator rewedge.  Unit 5 returned to service at 1645 on 21 March following turbine release pipe removal.  Unit 4 was out of service from 0418-1428 on 23 March due to regulator trouble.

- The first powerhouse ice and trash sluiceway remained open this reporting week, and the second powerhouse sluiceway remained closed.

- Second powerhouse fish units remained in service with one exception.  The units were out of service from 1442-1536 on 21 March for surveying.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

2.1. AWS Closures.  There were no AWS closures this reporting week.

2.2. Dewaterings and Fish Salvage.  Unit 5 tailogs were removed on 21 March in preparation for returning the unit to service following turbine release pipe removal.  Project biologists recovered 9 small sturgeon from the tailogs.  All fish were released in good condition.

2.3. STS Inspections.  One units’ STS’s were inspected this reporting week.  All screens were in good condition unless otherwise noted below.  See Table 1.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 9 | 3/23 | 687 | Replaced B-slot screen |

Table 1.  STS Inspection Data.

- RESEARCH.

3.1. AFC&MF Adult PIT-tag Interrogation.  NMFS has completed enlarging the orifices of the six weirs in the AFC&MF return ladder from 18” to 26”.  Hydraulic conditions were observed on 24 March which indicated the need for stoplogs to be installed on the overflow portion of the weirs to prevent any overflow as part of the test design.  They will be testing the detectors using PIT-tagged adult chinook and steelhead from the lab to get estimates of reading efficiencies for the 18” and 26” orifices.  They will be running several tests throughout the season with the first beginning in mid April.

3.2. PH2 Bypass System Evaluation.  NMFS released PIT tagged juvenile chinook and steelhead through the new bypass system to determine coil and 3-way rotational gate efficiency at the JMF this reporting week.  They will resume releases in May as part of their post construction evaluation to determine if fish condition is adversely affected by system passage.

3.3. PSMFC Smolt Monitoring.  NMFS continued 24-h/d PIT tag interrogation at PH2 JMF.  They are collecting fish for approximately 10 minutes per hour and sampling daily at 0800.

3.4. WDFW Fish Counting.  WDFW continued 24-h/d video counting at Bradford Island and Washington shore.

4.  FISHWAYS.  Project biologists inspected on 20, 21, 22, and 24 March this reporting week.

4.1. Fish Passage Plan Observations.  There were no Fish Passage Plan deviations this reporting week.

4.2. Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder below the count station at Washington shore.  Temperatures are supplied by The Fisheries Field Unit.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 3/19 | 6.5 | 6.5 |
| 3/20 | 6.6 | 6.6 |
| 3/21 | 6.8 | 6.8 |
| 3/22 | 7.0 | 7.0 |
| 3/23 | 7.1 | 7.1 |
| 3/24 | 7.2 | 7.2 |
| 3/25 | 7.2 | 7.2 |

Fish Ladder Temperatures (C)

4.3. Sensor Calibration.  Water level sensors were checked for calibration on 23 March this reporting week.

4.4. Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//