### CENWP-OP-B                                                                                               16 October 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 41 of 2000, which covers the period 08 October through 12 October.

- OPERATION SUMMARY.

  - Average daily river flow ranged from 102.9 to 123.7 kcfs.  Average daily tailwater elevation for the project ranged from 10.0’ to 11.5’ msl.  Average daily forebay elevation for the project ranged from 73.8’ to 75.0’ msl.  River temperature ranged between 61 and 63° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

  - Unit 3 remained out of service for turbine rehab.  Unit 13 remained out of service for four-year overhaul.  Unit 6 remained out of service for 100-day inspection.  On 11 October the following units went out of service for transducer removal dives; Unit 7 from 0512 until 0954, Units 9 and 10 from 0912 until 1248, Unit 11 from 1248 until 1406, and Unit 12 from 1406 until 1618.  On 12 October the following units went out of service for transducer removal dives; Unit 14 from 0500 until 1042, Unit 15 from 0942 until 1200, Unit 16 from 1042 until 1300, Unit 17 from 1200 until 1436, and Unit 18 from 1300 until 1554.  Unit 18 went out of service at 1624 12 October due to governor control problems.

  - Second powerhouse fish unit 1 went out of service from 0318 until 1712 10 October for slip ring maintenance.  Fish unit 2 went out of service from 0454 until 1706 11 October for slip ring maintenance.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.  No AWS closures.

  - Dewatering and Fish Salvage.  No fish salvage this week.

  - STS Inspections.  No STS inspections this reporting week.

3.   RESEARCH.

  - AFC&MF Adult PIT-tag Interrogation.  The 26” orifice inserts and shields were installed in the return ladder of the AFC&MF.  NMFS is testing and PIT-tagging adults from the lab to get estimates of reading efficiencies for the 26” orifice inserts.

  - AFC&MF Adult Sampling and Tagging.  The University of Idaho continues radio tagging and tracking adult Chinook for their adult telemetry research.  They are currently sampling 7 days per week.  ODFW and WDFW are sampling adult Chinook and steelhead approximately 2 days per week for their age composition research.  CRITFC completed their sampling this week.

  - Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

  - Normandeau/Mid-Columbia Consulting/Battelle PH2 Sluicechute Survival Testing.  Researchers  completed releasing balloon tagged fish through the second powerhouse ice and trash sluiceway for survival testing.  This work was in support of corner collector development.

  - NMFS Lamprey Tagging and Radio Tracking.  NMFS continues trapping and tagging lamprey in the AFC&MF.  They are releasing the radio tagged fish downstream and tracking the fish back through the project in cooperation with the University of Idaho.

  - PSMFC DSM1 and JMF Smolt Monitoring.  PSMFC finished 24-h/d PIT tag interrogation at DSM1.  They continue PIT tag interrogation and 24 h/d sampling at PH2 JMF.

  - University of Idaho Lamprey Test Flume.  The University of Idaho continues testing lamprey-swimming capabilities under various flow conditions in the lamprey test flume at the AFC&MF.

  - WDFW Fish Counting.  WDFW continues 16-h/d visual and 8-h/d video counting at Bradford Island and Washington shore.

  - WDFW/ODFW Fall Chinook counting.  WDFW and ODFW are still counting Fall Chinook at the Bradford Island and Washington shore count stations during the day.

4.  FISHWAYS.

  - Project biologists inspected on 10, 11, and 12 October this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week | Cascades Island diffuser FG6-18. | Diffuser is stuck partially open and should be closed. | Unknown. | Will repair during winter maintenance period. |
| All week. | PH1 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps per the FPP. | Unknown. | Investigating alternative method of measure. |
| All week | Cascade Island bird wires. | One wire is down. | Rangers cut wire to remove entangled gull. | Will repair during winter maintenance period. |
| 10/11 | PH2 collection channel electronic velocity meter. | Meter working intermittently. | Unknown. | Investigating alternative method of measure. |

  - Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are supplied by Fisheries Field Unit.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 10/8 | 16.2 | 16.1 |
| 10/9 | 16.5 | 16.3 |
| 10/10 | 16.1 | 16.0 |
| 10/11 | 15.9 | 15.8 |
| 10/12 | 15.8 | 15.7 |
| 10/13 | 15.6 | 15.5 |
| 10/14 | 15.4 | 15.3 |

Fish Ladder Temperatures (C)

  - Sensor Calibration.  Water level sensors were checked for calibration on 11 October this reporting week.  Weir gate 2 was out of calibration.  A work action request was submitted.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - FG3-3 was in manual control, after it stopped controlling properly, from 0330 9 October until 0830 10 October.  FG3-4 was placed in manual and open until FG3-3 was repaired at 0830 10 October.

  - The second powerhouse fishway was set up for single fish unit operation from 0318 10 October until 1706 11 October while the fish units underwent slip ring maintenance.

  - First powerhouse Ice and Trash Sluiceway was closed from 0755 until 1232 11 October for dive work.

  - The Add-in water valve for DSM2 was open 83% from 0510 until 1030 12 October while units 13 and 14 were shut down for the dive work.  One adult salmonid was seen behind the Add-in perf plate.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//