### CENWP-OP-B                                                                                               23 October 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 42 of 2000, which covers the period 15 October through 21 October.

- OPERATION SUMMARY.

  - Average daily river flow ranged from 105.7 to 119.5 kcfs.  Average daily tailwater elevation for the project ranged from 10.0’ to 12.2’ msl.  Average daily forebay elevation for the project ranged from 74.7’ to 75.0’ msl.  River temperature ranged between 60 and 62° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island ladder and Bradford Island ladder respectively, remain open 4”.

  - Unit 3 remained out of service for turbine rehab.  Unit 13 remained out of service for four-year overhaul.  Unit 6 remained out of service for 100-day inspection.  Unit 18 came back in service at 0724 16 October.  Unit 10 went out of service from 0912 until 1200 19 October for contractor inspection.

  - Second powerhouse fish units operated normally this reporting week.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.  No AWS closures.

  - Dewatering and Fish Salvage.  No fish salvage this week.

  - STS Inspections.  No STS inspections this reporting week.

3.   RESEARCH.

  - AFC&MF Adult PIT-tag Interrogation.  The 26” orifice inserts and shields were installed in the return ladder of the AFC&MF.  NMFS is testing and PIT-tagging adults from the lab to get estimates of reading efficiencies for the 26” orifice inserts.  Testing the shields was attempted 18 October.  Due to screen cleaner failure, the testing couldn’t be completed.

  - AFC&MF Adult Sampling and Tagging.  The University of Idaho continues radio tagging and tracking adult Chinook for their adult telemetry research.  They are currently sampling 7 days per week.  ODFW and WDFW are sampling adult Chinook and steelhead approximately 2 days per week for their age composition research.

  - Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

  - NMFS Lamprey Tagging and Radio Tracking.  NMFS continues trapping and tagging lamprey in the AFC&MF.  They are releasing the radio tagged fish downstream and tracking the fish back through the project in cooperation with the University of Idaho.

  - PSMFC DSM1 and JMF Smolt Monitoring.  PSMFC finished 24-h/d PIT tag interrogation at DSM1.  They continue PIT tag interrogation and 24 h/d sampling at PH2 JMF.

  - University of Idaho Lamprey Test Flume.  The University of Idaho continues testing lamprey-swimming capabilities under various flow conditions in the lamprey test flume at the AFC&MF.

  - WDFW Fish Counting.  WDFW continues 16-h/d visual and 8-h/d video counting at Bradford Island and Washington shore.

  - WDFW/ODFW Fall Chinook counting.  WDFW and ODFW are still counting Fall Chinook at the Bradford Island and Washington shore count stations during the day.

4.  FISHWAYS.

  - Project biologists inspected on 10, 11, and 12 October this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week | Cascades Island diffuser FG6-18. | Diffuser is stuck partially open and should be closed. | Unknown. | Will repair during winter maintenance period. |
| All week. | PH1 and PH2 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps per the FPP. | Unknown. | Investigating alternative method of measure. |
| All week | Cascade Island bird wires. | One wire is down. | Rangers cut wire to remove entangled gull. | Will repair during winter maintenance period. |

  - Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are supplied by Fisheries Field Unit.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 10/15 | 15.4 | 15.2 |
| 10/16 | 15.4 | 15.3 |
| 10/17 | 15.4 | 15.3 |
| 10/18 | 15.5 | 15.4 |
| 10/19 | 15.5 | 15.3 |
| 10/20 | 15.4 | 15.3 |
| 10/21 | 15.2 | 15.1 |

Fish Ladder Temperatures (C)

  - Sensor Calibration.  Water level sensors were checked for calibration on 19 October this reporting week.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - Because of mechanical reasons, DSM 2 screen cleaners were placed in manual from 1600 15 October until 0900 17 October.  During this time they were run twice per shift.  NMFS requested continuous running of DSM2 screen cleaners for their testing 0836 18 October.  At 1000 the screen cleaners timed out.  Mechanics found the chain had stretched and fallen off of the screen cleaner.  By 1410 the screen cleaner was back in auto and in continuous mode.  As NMFS couldn’t finish their testing, the screen cleaners were placed back on a three hour cycle.  Mechanics told us that the screen cleaner chain is going to break again and running it in its current condition will place strain on the gear boxes.  They recommended we reduce the frequency with which we run the sweeps.  DSM2 screen cleaners were placed in manual and are to be run once per shift (or more often depending on debris loads) to reduce wear and tear on the equipment.  New parts are on order.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//