### CENWP-OP-B                                                                                               18 December, 2000

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 50 of 2000, which covers the period 10 through 16 December.

- OPERATION SUMMARY.

  - Average daily river flow ranged from 137.2 to 175.9 kcfs.  Average daily tailwater elevation for the project ranged from 12.9’ to 15.4’ msl.  Average daily forebay elevation for the project ranged from 73.1’ to 75.6’ msl.  River temperature ranged between 45 and 48° F.  Spill bay 1, which supplies attraction flow for Cascades Island ladder, remained open 4”.  Spill bay 18, which supplies attraction flow for Bradford Island ladder, remains on seal.

  - Unit 3 remained out of service for turbine rehab.

  - Fish Unit 1 went to standby from 1424 until 1530 11 December to troubleshoot the auto regulator.  It returned to service though the regulator still didn’t work due to a bad 13X relay.  Second powerhouse fish units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.  Bradford Island AWS remains closed while the ladder is dewatered.

  - STS Inspections.  No STS’s were inspected this reporting week.

  - Dewatering and Fish Salvage.   No fish salvage this reporting week.

3.   RESEARCH.

  - AFC&MF Adult PIT-tag Interrogation.  The 26” orifice inserts and shields remain installed in the return ladder of the AFC&MF.

  - AFC&MF Adult Sampling and Tagging. WDFW is sampling adult steelhead approximately 7 days per week, throughout the winter, for age composition research.

  - Fisheries Field Unit Video Monitoring.  The Fisheries Field Unit is assisting NMFS adult PIT-tag interrogation work this year during their testing at the AFC&MF.  They are monitoring submerged orifice and overflow weir passage in the return ladder of the AFC&MF and assisting NMFS in verifying passage of streamer-marked PIT-tag fish during their testing.  They are also periodically monitoring submerged orifice and overflow weir passage at Cascades Island and Washington Shore ladders this year.

  - NMFS Lamprey Tagging and Radio Tracking.  NMFS completed trapping and tagging lamprey in the AFC&MF.  They are still tracking the fish back through the project in cooperation with the University of Idaho.

  - WDFW Fish Counting.  WDFW continues 24-h/d video counting at Washington shore.

4.  FISHWAYS.

  - Project biologists inspected on 11, 12, and 13 December this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week | Cascades Island diffuser FG6-18. | Diffuser is stuck partially open and should be closed. | Unknown. | Will repair during winter maintenance period. |
| All week. | PH2 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps per the FPP. | Unknown. | Investigating alternative method of measure. |
| All week | Cascade Island bird wires. | One wire is down. | Rangers cut wire to remove entangled gull. | Will repair during winter maintenance period. |
| 12/12 | Chain Gate 7A | Gate was closed. Should be set to 72’ msl. | Riggers are unable to remove the bulkhead in the slot. | Waiting for the proper equipment to remove bulkhead. |
| 12/12, 12/13 | Weir 37 | Weir reading >1 +/- .1’ | Unknown | Operators adjusting FV6-9 and inspecting the float for Weir 37. |

  - Fish Ladder Temperatures.  Readings are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Thermometers are currently undergoing calibration.

  - Sensor Calibration.  Water level sensors were checked for calibration on 13 December this reporting week.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - Because of mechanical reasons, DSM2 screen cleaners are run once per shift (or more often depending on debris loads) to reduce wear and tear on the equipment.

  - Units 11 and 12 are scheduled to be on standby from 06 December until 10 December to facilitate the drilling in the second powerhouse tailrace.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//