### CENWP-OP-B                                                                                               12 February 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 06 of 2001, which covers the period 04 through 10 February.

- OPERATION SUMMARY.

  - Daily river flow averaged 119.3 to 127.8 kcfs.  Daily project tailwater elevation averaged 11.7’ msl.  Daily project forebay elevation averaged 72.3’ to 74.5’ msl.  River temperature averaged 43 to 44° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, were closed to conserve water.

  - Unit 3 remained out of service for turbine rehab.   Unit 15 remained out of service for gate slot modifications.  Unit 4 went out of service at 0500 on 5 February until 1312 on 9 February for thrust bearing work.  Unit 2 went out of service from 0500 until 1300 on 8 February for thrust bearing cleaning.

  - Fish Units 1 and 2 remain out of service for annual maintenance.

- ACTIVITIES.

  - AWS Closures.  FV6-9 remains out of service while the Washington Shore ladder is dewatered.  FV5-3, FV5-4, and FV5-9 remain out of service while Cascades Island fishway is dewatered.

  - STS Inspections.  STSs are pulled from all units.

  - Dewatering and Fish Salvage.   On February 6th one wild adult summer steelhead was removed from the monitoring facility bypass flume.  The PSMFC biologist and a FFU biologist released the fish back to the river.

  - Second Powerhouse Fish Passage Flume.  On 6 February, biologists inspected the dewatered flume for structural problems and debris accumulations.  Biologists found nothing anomalous in the pipe.

3.   RESEARCH.

  - NMFS Lamprey Tagging and Radio Tracking.  NMFS completed trapping and tagging lamprey in the AFC&MF.  They are still tracking the fish back through the project in cooperation with the University of Idaho.

  - WDFW Fish Counting.  WDFW continues 24-h/d video counting at Bradford Island.

4.  FISHWAYS.

  - Project biologists inspected on 05, 06, 08, and 09 February this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week. | PH1 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps. | Unknown. | Waiting on new velocity meters. |
| All week | Cascade Island bird wires. | One wire is down. | Rangers cut wire to remove entangled gull. | Will repair during winter maintenance. |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Thermometers are currently undergoing calibration.

  - Sensor Calibration.  Water level sensors were checked for calibration on 08 February this reporting week.  Weir gate 1 was reading .4’ higher and weir gate 2 was reading 1.6’ lower.  A WAR was turned in to the electricians.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - DSM2 remains out of service for winter maintenance and follow on contract work.

  - Cascades Island and Washington Shore ladders remain out of service.

  - DSM1 remains out of service for water conservation.

  - The Ice and Trash Sluiceway at the First Powerhouse remains closed to conserve water.  If temperatures drop below freezing, the ITS will be opened as needed.  All chain gates were closed as well.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//