### CENWP-OP-B                                                                                                                                   30 April 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 17 of 2001, which covers the period 22 through 28 April.

- OPERATION SUMMARY.

  - Daily river flow averaged 93.5 to 131.6kcfs.  Daily spill averaged 0 kcfs.  Daily project tailwater elevation averaged 9.4’ to 12.4 msl.  Daily project forebay elevation averaged 74.4’ to 75.6’ msl.  River temperature averaged 51 to 55° F.  Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4” during daylight hours.  They are closed for water conservation between sunset and one hour before sunrise per BPA request.

  - Unit 3 remained out of service for turbine rehab.  Unit 15 went out of service from 1730 until 2312 on 23April for STS removal and FGE work.  Unit 15 will be used only for FGE testing from now until 15 July.

  - Powerhouse Two fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.   FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is installed.

  - STS/VBS Inspections.  STSs were removed from Unit 15 on 23 April to accommodate FGE/OPE tests.

  - Dewatering and Fish Salvage.   No fish salvage this week.

3.   RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is under construction.  Fish collection is scheduled to begin in early May.

  - OCFWRU Barging condition study.  Began 24 April.

  - ODFW Pikeminnow electrofishing.  Capture and tagging program for pikeminnow, smallmouth bass, and walleye in the tailrace and forebay occurred last week.   They are done for this year.

  - PSMFC Adult PIT.  Chinook are collected and tagged on Wednesdays.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  Monitoring at DSM1 continues.

  - WES Hydroacoustic Monitoring.  Transducers are installed at Units 1-5 and Units 7-10.  Monitoring began  20 April.

  - UI Barging condition study. They began sampling juvenile fish from transport barges on 22 April.

  - USGS Juvenile Radiotracking.  Radio tagging began 1 April.  First release from Hood River bridge is expected to occur on 1 May.

  - USGS Adult EMG tracking.  Underwater and aerial antennas are installed around Bradford Island and on the pier noses of the spillway.  Fish release and tracking began 18 April.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at Powerhouse One are operated according to UI request.  This will continue until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of the season.

  - CRITFC/ODFW.  Tagging Spring Chinook and steelhead on Tuesdays and Thursdays, with Friday as an extra day if needed.

  - WDFW.  Tagging Spring Chinook with jaw tags in conjunction with their tooth-net studies.

4.  FISHWAYS.

  - Project biologists inspected on 22, 23, 25, and 26 April this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week. | PH1and PH2 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps. | Unknown. | New velocity meters to be installed during mid-season dives. |
| 4/23. | Weirs 37 and 38 | Less than 1.0’ water elevation. | AFF dewatering activities. | Back to normal by 1000. |
| 4/25 | FG3-26, FG3-27 | Diffusers were closed. | Diffusers are operated in manual. | Operators went to check tailwater elevations and make corrections. |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 4/22 | 9.6 | 9.6 |
| 4/23 | 9.6 | 9.6 |
| 4/24 | 9.8 | 9.8 |
| 4/25 | 10.1 | 10.1 |
| 4/26 | 10.7 | 10.7 |
| 4/27 | 10.8 | 10.9 |
| 4/28 | 11.1 | 11.1 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 23 April this reporting week.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - PH1 Collection channel electricity was interrupted after a wire went to ground on 26 April.  The condition persisted from approximately 0800 until 1430.  There was no control over the entrance gates during that time.  Entrance gates were in criteria as of 0800.  Tailwater did not change substantially during the day, so gates remained close to proper elevation.  Electricians repaired the wire.

  - The high outfall hydrocannons for the Second Powerhouse monitoring facility remain in service.

  - Though Unit 15 is only being used for FGE/OPE testing, the orifices are still open.  11A-S remains in auto.

  - DSM2 Add-in water remains in operation.  Six dead smolts were removed from the perf plate between 24 and 25 April.  One live smolt was seen behind the perf plate on 25 April.

  - All week long there were reports of seals or sea lions in the tailraces of both powerhouses.  The Project did not take any action towards removing the natural predators from the river system.

  - DSM2 screen cleaners returned to auto at 1530 on 23 April.

GENE L. LADOUCEUR

# Operations Project Manager

//S//