### CENWP-OP-B                                                                                                                                   14 May 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 19 of 2001, which covers the period 06 through 12 May.

- OPERATION SUMMARY.

  - Daily river flow averaged 109.3 to 148.1kcfs.  Daily spill averaged 0 kcfs.  Daily project tailwater elevation averaged 10.7’ to 13.5’ msl.  Daily project forebay elevation averaged 74.5’ to 75.6’ msl.  River temperature averaged 56 to 57° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4” during daylight hours.  They are closed for water conservation between sunset and one hour before sunrise per BPA request.

  - Unit 3 remained out of service for turbine rehab.  Unit 15 was out of service due to a governor lock up from 2342 07 May until 1106 08 May.  Unit 15 will be placed on standby each night after FGE testing as of 09 May.  Unit 8 was out of service due to an ESBS motor problem from 0430 08 May until 0912 09 May.

  - Powerhouse Two fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.   FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is installed.

  - STS/VBS Inspections.  Video inspection results of STS/VBS screens include the following units.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 1 | 5/10 | 214 |  |
| 2 | 5/10 | 538 |  |
| 4 | 5/10 | 294 |  |
| 5 | 5/9 | 288 |  |
| 6 | 5/9 | 326 |  |
| 7 | 5/9 | 268 |  |
| 8 | 5/9 |  | Replace broken ESBS electric motor |
| 9 | 5/9 | 366 |  |
| 10 | 5/9 | 464 |  |
| 16 | 5/10 | 688 |  |

  - Dewatering and Fish Salvage.   No fish salvage this week.

3.   RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility to begin operating on 11 May.

  - OCFWRU Barging condition study.  Began 24 April.

  - ODFW Pikeminnow electrofishing.  Done for this year.

  - PSMFC Adult PIT.  Chinook are collected and tagged on Wednesdays.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  Monitoring at DSM1 continues.

  - WES Hydroacoustic Monitoring.  Transducers are installed at Units 1-5 and Units 7-10.  Monitoring began  20 April.

  - UI Barging condition study. They began sampling juvenile fish from transport barges on 22 April.

  - USGS Juvenile Radiotracking.  Radio tagging began 1 April.  Tracking in progress as well.

  - USGS Adult EMG tracking.  Fish release and tracking began 18 April.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at Powerhouse One operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.

  - CRITFC/ODFW.  Tagging Spring Chinook and steelhead on Tuesdays and Thursdays, with Friday as an extra day if needed.

  - WDFW.  Tagging Spring Chinook with jaw tags in conjunction with their tooth-net studies.

4.  FISHWAYS.

  - Project biologists inspected on 07, 08, and 09 May this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week. | PH1and PH2 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps. | Unknown. | New velocity meters to be installed during mid-season dives. |
| 5/9 | Upper Switchgate | Monitoring facility to bypass. | Repairs on the two way rotating gate. | Outage coordinated and minimized to the extent possible. |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/05 | 12.0 | 11.9 |
| 5/06 | 12.2 | 12.2 |
| 5/07 | 12.5 | 12.5 |
| 5/08 | 12.8 | 12.7 |
| 5/09 | 12.8 | 12.8 |
| 5/10 | 12.9 | 12.9 |
| 5/11 | 13.2 | 13.1 |
| 5/12 | 13.5 | 13.5 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 09 May this reporting week.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - DSM2 Add-in water remains in operation.  18 dead smolts were removed from the perf plate 06 May, five were removed 07 May, 10 were removed 08 May, and one live smolt was spotted behind the perf plate 09 May.  As of 08 May, Add-in flow has been shut off and a caution order tag hung on the valve.

  - 11A-S remains closed in manual.

  - The high outfall hydrocannons for the Second Powerhouse monitoring facility remain in service.

  - Though Unit 15 is only being used for FGE/OPE testing, the orifices are still open.

  - Throughout the week there were reports of seals or sea lions in the tailraces of both powerhouses.  The Project did not take any action towards removing the natural predators from the river system.

GENE L. LADOUCEUR

# Operations Project Manager

//S//