### CENWP-OP-B                                                                                                                                   04 June 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 22 of 2001, which covers the period 27 May through 02 June.

- OPERATION SUMMARY.

  - Daily river flow averaged 121.4 to 174.9kcfs.  Daily spill averaged 49.3 to 49.8 kcfs.  Daily project tailwater elevation averaged 11.5’ to 15.2’ msl.  Daily project forebay elevation averaged 74.6’ to 75.5’ msl.  River temperature averaged 61 to 62° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4” during daylight hours.  They are closed for water conservation between sunset and one hour before sunrise per BPA request.

  - Unit 3 remained out of service for turbine rehab. Unit 15 is placed on standby each night after FGE testing.  Unit 1 went out of service from 1912 on 28 May until 1054 on 02 June for pre-rehab work.  Unit 17 went out of service for a four-year overhaul at 0848 on 29 May.

  - Powerhouse Two fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are being placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.   FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is installed.

  - STS/VBS Inspections.  Inspection results of STS screens include the following units.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 5/31 | 667 |  |
| 12 | 5/30 | 619 |  |
| 13 | 5/30 | 485 |  |
| 14 | 5/30 | 497 |  |
| 15 | 5/31 | 325 | Video inspection of STS and VBS |
| 16 | 5/30 | 403 |  |
| 17 | 5/29 | 639 | STSs pulled. Unit down for overhaul. |
| 18 | 5/31 | 667 |  |

  - Dewatering and Fish Salvage.  Project biologists recovered 28 sturgeon, 5 channel catfish, 1 sculpin, and 3 dead juvenile Chinook from the Unit 17 draft tube on 30 May.

3.   RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.

  - OCFWRU Barging condition study.  Began 24 April.

  - PSMFC Adult PIT.  Chinook are collected and tagged on Wednesdays.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  Monitoring at DSM1 also continues.

  - WES Hydroacoustic Monitoring.  Monitoring began 20 April.

  - UI Barging condition study. They began sampling juvenile fish from transport barges on 22 April.

  - USGS Juvenile Radiotracking.  Radio tagging began 1 April.  Tracking in progress as well.

  - USGS Adult EMG tracking.  Fish release and tracking began 18 April.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at Powerhouse One operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.

  - CRITFC/ODFW.  Tagging Spring Chinook and steelhead on Tuesdays and Thursdays.

  - WDFW.  Tagging Spring Chinook with jaw tags in conjunction with their tooth-net studies.

  - NMFS FGE/OPE.  Work began 23 April.  Spring testing ended ~ 23 May.  Summer tests begin ~19 June.

4.  FISHWAYS.

  - Project biologists inspected on 29, 30, 31 May and 01 June this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE |
| --- | --- | --- | --- | --- |
| All week. | PH1and PH2 collection channel electronic velocity meter. | Meter was not working and should register 1.5-4.0 fps. | Unknown. | New velocity meters to be installed during mid-season dives. |
| 5/29 | SDE gate | Less than 13.0’ opening. | Unknown | Operators to check and manually operate. |
| 5/29 | OG/SG 34 | Gate was closed in manual, should be in auto for UI studies. | Unknown | Operator put gate in auto. |
| 5/29 | FG3-25, FG3-24 | Not in correct position for tailwater elevation. | Computer system not yet installed, all diffusers are operated in manual. | Operator corrected diffuser positioning |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/27 | 16.2 | 16.3 |
| 5/28 | 15.8 | 15.8 |
| 5/29 | 15.7 | 15.6 |
| 5/30 | 15.7 | 15.6 |
| 5/31 | 15.9 | 15.9 |
| 6/1 | 16.3 | 16.2 |
| 6/2 | 16.3 | 16.1 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 31 May this reporting week.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - F2A-N and F2B-N orifices will remain open as of 29 May while the Add-in is closed.

GENE L. LADOUCEUR

# Operations Project Manager

//S//