### CENWP-OP-B                                                                                                                                  9 July 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 27 of 2001, which covers the period 01 through 07 July.

- OPERATION SUMMARY.

  - Daily river flow averaged 85.1 to 126.3kcfs.  Daily spill averaged 0.0 kcfs.  Daily project tailwater elevation averaged 8.5’ to 11.6’ msl.  Daily project forebay elevation averaged 73.9’ to 74.7’ msl.  River temperature averaged 64 to 66° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4” during daylight hours.

  - Unit 3 remained out of service for turbine rehab.  Unit 17 remains out of service for its four-year overhaul.  Unit 5 remains out of service for turbine rehab.  Unit 15 FGE summer tests began 15 June.  The unit is on standby each night following FGE testing.  Unit 9 was forced out of service from 0424 until 2330 on 01 July due to a tripped bearing oil pump.

  - Powerhouse Two fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.   FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is installed.  FV3-9 was closed for cleaning from 1900 until 1912 on 01 July.   FV3-7 was closed for cleaning from 0815 until 1145 on 05 July.

  - STS/VBS Inspections.  No STS inspections this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage this reporting week.

- RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - OCFWRU Barging Condition.  Sampling to end 13 July.

  - PSMFC Adult PIT.  Looking at A and B branch and Cascade Island for noise interference.  Analyzing data collected at the Washington Shore ladder.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  24 h/d flat plate monitoring at DSM1.

  - WES Hydroacoustic Monitoring.  Monitoring began 20 April.  Should be complete by 15 July.  Equipment removal scheduled 30 July – 9 August.

  - UI Barging Condition and Separation By Code study.  Summer studies complete.  Will conduct fall chinook separation by code study 15 July through 17 September.

  - USGS Juvenile Radiotracking.  Radio tagging began 1 April.  Tracking is expected to be complete by 31 July.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at Powerhouse One are being operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.

  - CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging Spring Chinook and steelhead on Tuesdays and Thursdays.

  - WDFW.  Completed jaw-tagging Chinook for tooth-net studies.

  - NMFS FGE/OPE.  Work began 23 April.  Spring testing ended ~ 23 May.  Summer tests began 11 June and should be complete by 13 July.

  - NMFS Lamprey.  Lamprey are tagged and tracked throughout the week.  Spillway ladder entrances manually operated at night for a .5’ differential.  NMFS is holding extra lamprey for the Warm Springs Tribe, and collecting fish for USGS.

  - Pelfrey Sturgeon Hatchery.  Broodstock collection in PH1 tailrace completed.

  - YIN Northern Pikeminnow Dam Angling.  Fishing 25 June – 30 September.

4.  FISHWAYS.

  - Project biologists inspected every day (01-07 July) this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | PH2 is not yet working. | Not fully installed. | New velocity meters installed in channel, awaiting core drilling at PH2. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers are being designed, and will be installed during winter maintenance. | 20013904 |
| All week | PH1 Collection channel velocity | Velocity meter registers less than 1.5 fps | Velocity meter in a slow area of the channel. | Velocity improves when OG/SG gates are open. FFU looking at the flow model, will suggest possible solutions. |  |
| All week | FG3-26 | Not in correct position for TW elevation. | Computer system not yet installed, all B-branch diffusers in manual. | Operator corrected diffuser positioning. |  |
| 7/1, 7/6, 7/7 | FG3-27 | Not in correct position for TW elevation. | FG3-27 is open to supplement FG3-28 | No action taken. |  |
| 7/7 | FG6-14 | Not in correct position for TW elevation. | Computer system not yet installed, all Cascade Island diffusers in manual | Operator corrected diffuser positioning |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 7/1 | 18.1 | 18.0 |
| 7/2 | 18.3 | 18.1 |
| 7/3 | 18.5 | 18.4 |
| 7/4 | 18.8 | 18.8 |
| 7/5 | 18.7 | 18.8 |
| 7/6 | 18.5 | 18.5 |
| 7/7 | 18.6 | 18.5 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 6 July.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - 12 dead lamprey are floating in the Cascade Island ladder above the count station.  They got into the ladder before the perforated bulkhead was lowered on 31 May.

  - PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.  We plan no further action at this time.

  - FV3-9 was placed in manual from 1930 on 01 July until 0330 on 02 July.  The float got stuck and the valve failed to control properly.

  - PH1 Collection Channel velocity is very low when orifice block tests require orifices be closed.  We can overcome the problem when tailwater is greater than or equal to 10 ‘.  Tailwater is dropping lower than that now, so the channel is sometimes out of criteria.  We continue working with FFU and District Bios to find a solution.

  - Spill stopped at 0000 16 June.  All bays are on seal during evening hours.  Bays 1 and 18 will remain open 4” during daylight hours.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//