### CENWP-OP-B                                                                                                                                  22 July 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 29 of 2001, which covers the period 15 through 21 July.

- OPERATION SUMMARY.

  - Daily river flow averaged 75.9 to 105.3kcfs.  Daily spill averaged 0.0 kcfs.  Daily project tailwater elevation averaged 7.3’ to 9.8’ msl.  Daily project forebay elevation averaged 74.4’ to 75.6’ msl.  River temperature averaged 65 to 67° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4” during daylight hours.

  - Unit 3 remained out of service for turbine rehab.  Unit 17 remains out of service for its four-year overhaul.  Unit 5 remains out of service for turbine rehab.  Units 6, 7, and 8 went out of service at 0500 on 16 July for roof disconnect work.  Unit 16 went out of service from 0440 until 1742 on 16 July for annual maintenance.  Unit 13 went out of service from 0948 until 1442 on 18 July for STS repair.  Unit 4 went out of service from 2112 on 18 July until 0900 on 19 July for STS repair.

  - Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

- ACTIVITIES.

  - AWS Closures.   FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is installed.   On 19 July the B-branch computer went into service.  FV4-4 is still in manual until the elevation pool sensor has been properly calibrated.

  - STS/VBS Inspections.  STSs were not inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage this reporting week.

- RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - PSMFC Adult PIT.  Looking at A and B branch and Cascade Island for noise interference.  Analyzing data collected at the Washington Shore ladder.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  24 h/d flat plate monitoring at DSM1.

  - WES Hydroacoustic Monitoring.  Equipment removal scheduled 30 July – 9 August.

  - UI Barging Condition and Separation By Code study.  Fall chinook separation by code study runs 15 July through 17 September.

  - USGS Juvenile Radiotracking.  Radiotracking study completed.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at Powerhouse One are being operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.

  - CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging Spring Chinook and steelhead on Tuesdays and Thursdays.

  - NMFS FGE/OPE.  Summer tests ended this week.

  - NMFS Lamprey.  Lamprey are tagged and tracked throughout the week.  Spillway ladder entrances manually operated at night for a .5’ differential.  NMFS is holding extra lamprey for the Warm Springs Tribe, and collecting fish for USGS.

  - YIN Northern Pikeminnow Dam Angling.  Fishing 25 June – 30 September.

4.  FISHWAYS.

  - Project biologists inspected every day (15-21July) this reporting week.  NMFS inspected on 16 July.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | PH2 is not yet working. | Not fully installed. | New velocity meter installed in channel, awaiting core drilling at PH2. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers are being designed, and will be installed during winter maintenance. | 20013904 |
| 7/18-19 | PH1 Collection channel velocity | Velocity meter registers less than 1.5 fps when testing requires orifice/sluice gates be closed. | Water backs up in the channel. | Velocity improves when OG/SG gates are open. Changing diffuser operations was moderately successful. Continuing to monitor situation. |  |
| All week | FG3-27 | Not in correct position for TW elevation. | FG3-27 is open to replace FG3-28. | No action taken. |  |
| 7/19 | FG6-14 | Not in correct position for TW elevation. | Computer system not yet installed, all Cascade Island diffusers in manual | Operator corrected diffuser positioning |  |
| 7/18, 7/19 | Entrance gates at B-Branch and Cascade Island Ladders. | Not in correct position for TW elevation. | Computer system not yet functioning. Both ladders are operated in manual | Operators corrected gate positioning. |  |
| 7/15, 7/17 | A branch water over weir | Staff gauge reads >1.5’ | Unknown | B-branch reads correctly, BI reads 1.2’ so no action taken. |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 7/15 | 19.5 | 19.4 |
| 7/16 | 19.0 | 19.0 |
| 7/17 | 18.9 | 18.8 |
| 7/18 | 19.0 | 18.8 |
| 7/19 | 19.2 | 19.1 |
| 7/20 | 19.2 | 19.1 |
| 7/21 | 19.1 | 19.0 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 19 July.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - Project removed TIES 16-18 July.

  - USDA Wildlife Services removed the spillway avian lines on 19 July to allow barge crane access (for spillway deflector installation).  The spillway wire grid will be re-installed in mid-April when spillway flow deflector work is complete.

  - PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.

  - Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.

  - Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.

  - Spill stopped at 0000 16 June.  All bays are on seal during evening hours.  Bays 1 and 18 will remain open 4” during daylight hours.

  - The B-Branch computer was installed on 19 July.  As soon at the Entrance Pool elevation sensor has been calibrated and the North and South entrance gates are connected properly, B-Branch will be back in auto operation.  Until then, the entrance gates and FV4-4 are still operated in manual.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//