### CENWP-OP-B                                                                                                                               27 August, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 34 of 2001, which covers the period 19 through 25 August.

- OPERATION SUMMARY.

  - Daily river flow averaged 85.7 to 107.9kcfs.  Daily spill averaged 49.4 to 49.8kcfs.  Daily project tailwater elevation averaged 8.1’ to 9.7’ msl.  Daily project forebay elevation averaged 74.7’ to 75.3’ msl.  River temperature averaged 68 to 69° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4”.  Twenty-four hour spill of 50kcfs began at 1400 on 09 August and will continue until further notice.

  - Unit 3 remains out of service for turbine rehab.  Unit 17 remains out of service for its four-year overhaul.  Unit 5 remains out of service for turbine rehab.  Unit 9 returned to service at 2136 on 20 August.  Unit 10 went out of service from 0530 until 2136 on 20 August for semi-annual maintenance.

  - Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.    F2 and F1 were idled for trash raking at 1440 and 1615, respectively, on 23 August.  Both units returned to normal operation at 1642 on 23 August.

- ACTIVITIES.

  - AWS Closures. FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is calibrated.   FV3-9 was closed for cleaning from 0646 until 0700 on 20 August.  FV5-9 was closed for cleaning from 0741 until 0751 on 20 August.

  - STS/VBS Inspections.  No STSs were video inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage this reporting week.

- RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - PSMFC Adult PIT.  Looking at A and B branch and Cascade Island for noise interference.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  All flat plate monitoring at DSM1 ended at 0800 on 02 August.

  - UI Barging Condition and Separation By Code study.  Fall Chinook separation by code study runs 15 July through 17 September.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at the first powerhouse are being operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.   Researchers are adding ice to the anesthetic tank when water temperatures approach 70° F.

  - CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging Chinook and steelhead on Tuesdays and Thursdays.

  - NMFS Lamprey.  Lamprey are tagged and tracked throughout the week.  Spillway ladder entrances manually operated at night for a .5’ differential.  NMFS is collecting fish for USGS.

  - YIN Northern Pikeminnow Dam Angling.  Fishing 25 June – 30 September.

  - WDFW/ODFW Fall Chinook Counting.  Observations of the fall Chinook continue.

4.  FISHWAYS.

  - Project biologists inspected 19 through 25 August this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | The velocity meter is not yet working. | Not fully installed. | Working on final installation. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers are being designed, and will be installed during winter maintenance. | 20013904 |
| All week | FG3-27 | Not in correct position for TW elev. | FG3-27 is open to replace FG3-28. | No action taken. |  |
| 8/19-21, 8/24-25 | PH1 Collection channel velocity | Velocity meter registers less than 1.5 fps. | Water backs up in the channel during OG/SG tests. | Monitoring situation. |  |
| All week | Main Dam Avian wires | Wires removed. | Spillway deflector installation. | Wire grid to be replaced in Mid-April. |  |
| 8/19 | WG37, UMT staff gauge | Water over weir too high. | Not yet in Non Shad passage mode. | Electricians reset limits. |  |
| 8/20-21, 8/24-25 | B-Branch staff gauge | Reading less than 1.0’ | Unknown. |  |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 8/19 | 21.3 | 21.2 |
| 8/20 | 21.3 | 21.1 |
| 8/21 | 21.0 | 20.9 |
| 8/22 | 21.0 | 20.7 |
| 8/23 | 21.0 | 20.8 |
| 8/24 | 21.2 | 21.0 |
| 8/25 | 21.4 | 21.2 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 24 August.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.

  - Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.

  - Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.

  - The B-Branch and Cascade Island computers were installed.  Sensors need calibrated and some parameters need setting.  Until then, entrance gates and FV4-3, 4-4, 5-3, and 5-4 are operated in manual.

  - Spillway avian wires were removed 19 July to facilitate deflector work.  Large flocks of gulls soon began feeding and roosting around the spillway.  This week, USDA Wildlife Services increased efforts to control avian predation around the spillway.

  - FV3-9 was in manual control from 0415 19 August until 0700 20 August due to a float control alarm that wouldn’t clear.   At this time, it appears to be working correctly.

  - PH2 Corner Collector exploratory drilling along the north side of Cascades Island continued.

  - Salmon Corps began volunteer work this week.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//