### CENWP-OP-B                                                                                                                           02 September, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 35 of 2001, which covers the period 26 August through 01 September.

- OPERATION SUMMARY.

  - Daily river flow averaged 94.4 to 124.1kcfs.  Daily spill averaged 0.0 to 49.9kcfs.  Daily project tailwater elevation averaged 8.8’ to 11.0’ msl.  Daily project forebay elevation averaged 75.0’ to 75.6’ msl.  River temperature averaged 69 to 70° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4”.  Twenty-four hour spill of 50kcfs began at 1400 on 09 August and ended at 2359 on 31 August.

  - Unit 3 remains out of service for turbine rehab.  Unit 17 remains out of service for its four-year overhaul.  Unit 5 remains out of service for turbine rehab.  Unit 7 went out of service from 1530 until 1654 on 27 August due to a broken governor linkage pin.

  - Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  F2 went to speed no load for trash raking from 1453 until 1625 on 29 August.

- ACTIVITIES.

  - AWS Closures. FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is calibrated.

  - STS/VBS Inspections.  Two STSs were video inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 8/28 | 810 |  |
| 18 | 8/28 | 806 |  |

Table 1.  STS/VBS Inspection Data.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage this reporting week.

- RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - PSMFC Adult PIT.  Looking at A and B branch and Cascade Island for noise interference.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the monitoring facility.  All flat plate monitoring at DSM1 ended at 0800 on 02 August.

  - UI Barging Condition and Separation By Code study.  Fall Chinook separation by code study runs 15 July through 17 September.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at the first powerhouse are being operated according to UI request until 31 October.  Tagging of Chinook began at the AFC&MF 2 April and will continue seven days a week until the end of September.   Researchers are adding ice to the anesthetic tank when water temperatures approach 70° F.

  - CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging Chinook and steelhead on Tuesdays and Thursdays.  One mortality reported on 31 August (see Misc. 5.13 below).

  - NMFS Lamprey.  Lamprey are tagged and tracked throughout the week.  Spillway ladder entrances manually operated at night for a .5’ differential.  NMFS is collecting fish for USGS.

  - YIN Northern Pikeminnow Dam Angling.  Fishing 25 June – 30 September.

  - WDFW/ODFW Fall Chinook Counting.  Observations of the fall Chinook continue.

4.  FISHWAYS.

  - Project biologists inspected 26 August through 01 September this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | The velocity meter is not yet working. | Not fully installed. | Working on final installation. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers are being designed, and will be installed during winter maintenance. | 20013904 |
| All week | FG3-27 | Not in correct position for TW elev. | FG3-27 is open to replace FG3-28. | No action taken. |  |
| 8/26-28, 8/30-31 | PH1 Collection channel velocity | Velocity meter registers less than 1.5 fps. | Water backs up in the channel during OG/SG tests. | Monitoring situation. |  |
| All week | Main Dam Avian wires | Wires removed. | Spillway deflector installation. | Wire grid to be replaced in Mid-April. |  |
| 8/27-31 | Bradford Island fish ladder weirs | Reading less than 1.0’ | FV3-9 won’t control to such a narrow band. | See Misc. 5.9 below. |  |
| 9/1 | Unit 11 and 12 orifice lights | All lights off. | Broken receptacle | Electrician called in. | 20014759 |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 8/26 | 21.6 | 21.4 |
| 8/27 | 21.8 | 21.6 |
| 8/28 | 21.7 | 21.7 |
| 8/29 | 21.8 | 21.7 |
| 8/30 | 21.9 | 21.8 |
| 8/31 | 21.7 | 21.7 |
| 9/1 | 21.5 | 21.4 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 30 August.

  - Zebra Mussel Monitoring.  The zebra mussel monitoring station was inspected and showed no signs of colonization this reporting week.

- MISCELLANEOUS

  - PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.

  - Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.

  - Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.

  - The B-Branch and Cascade Island computers were installed.  Sensors need calibrated and some parameters need setting.  Until then, entrance gates and FV4-3, 4-4, 5-3, and 5-4 are operated in manual.

  - Spillway avian wires were removed 19 July to facilitate deflector work.  Large flocks of gulls soon began feeding and roosting around the spillway.  USDA Wildlife Services has increased avian predation abatement around the spillway.

  - Completed PH2 Corner Collector exploratory drilling along the north side of Cascades Island.

  - Salmon Corps continue volunteer work.

  - One dead Chinook smolt was found on the grating by orifice 12 B-N the morning of 29 August.

  - In an effort to keep A and B branch “depth over weir” in criteria, the depth at the Bradford Island staff gauge will be increased to 1.0’ +/- .1’.  The FPP calls for .9’ water over weir, but at that depth, A and B Branches were reading .1-.2’ too low.

  - Non-shad “depth over weir” adjustments to Washington shore and Cascade Island ladders were completed on 27 August.

  - The JMF went to bypass from 0754 until 1605 on 28 August to facilitate PDS weir and vent work.  The modifications did not have the desired effect of preventing the end of the perf plate from drying out.

  - FV3-9 went to manual operation at 0830 on 1 September due to a failure to properly maintain water levels.  An electrician was called in to look at it.  TR#20014760.

  - CRITFC reported one dead Chinook on 31 August.  They believe it was a Tule and not an ESA listed fish.  Researchers photographed and measured the fish before returning it to the river.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//