### CENWP-OP-B                                                                                                                               15 October, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 41 of 2001, which covers the period 07 through 13 October.

- OPERATION SUMMARY.

  - Daily river flow averaged 72.3 to 93.2kcfs.   Daily project tailwater elevation averaged 6.8’ to 8.5’ msl.  Daily project forebay elevation averaged 74.3’ to 75.6’ msl.  River temperature averaged 62 to 64° F.

  - Spill bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, remain open 4”.  This translates to a daily spill average of 2.3kcfs.

  - Unit 3 remains out of service for turbine rehab.  Unit 17 returned to service at 1518 on 10 October.  Unit 5 remains out of service for turbine rehab.   Unit 11 was out of service from 1336 until 1636 on 09 October for STS repair work.  Units 6 went out of service for Bank 5/6 delta bus work from 0418 until 1430 on 12 October.  Unit 7 went out of service for switching work from 0418 until 0430 and again from 1200 on 12 October until 1436 on 13 October.  Unit 8 went out of service for switching work from 0418 until 0430 and from 1400 until 1430 on 12 October.  Unit 4 went out of service for work on Bank 3/4 delta bus from 1000 until 1524 on 13 October.

  - Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.    Fish Unit 1 went out of service for slipring maintenance from 0730 until 1548 on 09 October.  Fish Unit 2 went out of service for slipring maintenance from 0342 until 2112 on 10 October.

- ACTIVITIES.

  - AWS Closures. FV4-3 and FV4-4 at B-branch and FV5-3 and FV5-4 are all operating in manual until the new computer system is calibrated.  FV1-1 was closed for cleaning from 0800 until 0847 on 09 October.  The Bradford Island fishway exit was closed for cleaning from 1558 until 1610 on 10 October.

  - STS/VBS Inspections.  Six STSs were video inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 10/10 | 1013 | Shaft loose |
| 12 | 10/11 | 673 |  |
| 15 | 10/11 | 523 |  |
| 16 | 10/11 | 449 | Full of grass |
| 17 | 10/10 | 0 | Put in service |
| 18 | 10/10 | 1005 |  |

Table 1.  STS/VBS Inspection Data.

  - STS removal. PH1 STS remain OOS per NMFS request.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activity to report.

- RESEARCH.

  - WDFW Fish Counting.  WDFW continues 16-hour visual counts and 8-hour video counts at Bradford Island and Washington Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - PSMFC Adult PIT.  Tagging completed.  Planning for construction at the Bradford Island and Cascade Island ladders continues.

  - PSMFC Smolt Monitoring Program.  Collection continues 24h/d at the PH2 monitoring facility.

  - UI Adult Fallback. UI Adult Radiotracking/Tagging.  PCC entrance gates at the first powerhouse are being operated according to UI request until 31 October.  Tagging of Chinook reduced to 4 or 5 days a week until the middle of October.

  - CRITFC/ODFW/WDFW Adult Trapping/Tagging.  Tagging and trapping on Tuesdays and Wednesdays.

4.  FISHWAYS.

  - Project biologists inspected 07, 08, 09, 10, 12, and 13 October this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | The velocity meter is not yet working. | Not fully installed. | Working on final installation. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers are designed, and will be installed during winter maintenance. | 20013904 |
| All week | FG3-27 | Not in correct position for TW elev. | FG3-27 is open to replace FG3-28. | No action taken. |  |
| All week | PH1 Collection channel velocity | Velocity meter registers less than 1.5 fps. | Water backs up in the channel during OG/SG tests. | Monitoring situation. |  |
| All week | Main Dam Avian wires | Wires removed. | Spillway deflector installation. | Wire grid to be replaced in Mid-April. |  |
| 10/8-9 | Orifice 13A-S | Closed | Shaft has separated from the knife gate. | Operators put in local control. | 20012261 completed 10/13 |
| 10/12-13 | F2B-S | Closed | Faulty proximity switch. | Operators put in local control and open. | 20012337 completed10/15 |
| 10/13 | BI ladder | Low water over weir | Trashracks being cleaned. | No action taken. |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 10/07 | 17.8 | 17.6 |
| 10/08 | 17.6 | 17.4 |
| 10/09 | 17.3 | 17.2 |
| 10/10 | 16.9 | 16.8 |
| 10/11 | 16.6 | 16.5 |
| 10/12 | 16.4 | 16.2 |
| 10/13 | 16.2 | 16.1 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 12 October.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - PH2 JBS injury/mortality issue: Juvenile mortality remains low at the JMF, according to PSMFC reports.

  - Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.

  - Closed OG/SG testing causes low differential at the north end of PH1 collection channel.  FV1-1 normally controls south channel differential, but is now reprogrammed to maintain north channel differential.  This change should also help maintain proper collection channel velocity during OG/SG tests.

  - The B-Branch and Cascade Island computers were installed.  Sensors need calibrated and some parameters need setting.  Until then, entrance gates and FV4-3, 4-4, 5-3, and 5-4 are operated in manual.  Waiting on parts.

  - Weir 37 float control doesn’t adequately control water level over the weir.  A sonic transducer will be installed which should correct the problem.

  - The outfall hydrocannon remains off.  We have not observed any significant bird activity.

  - Powerhouse Two Ice and Trash Chute was open to pass trash from 0850 until 0903 on 9 October.

  - Powerhouse One Ice and Trash Sluiceway was closed for boat work in the BRZ from 0800 until 1645 on 12 October and from 0700 until 1418 on 13 October.

  - FFU reported a dead Coho at the Wave area on the Washington Shore on 10 October.  It appears to have jumped out of the ladder where the concrete had been cut to allow for DSM2/JMF improvements.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//