### CENWP-OP-B                                                                                                                          12 November, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 45 of 2001, which covers the period 04 through 10 November.

- OPERATION SUMMARY.

  - Daily river flow averaged 84.4 to 128.1kcfs.  Daily project tailwater elevation averaged 8.2’ to 10.8’ msl.  Daily project forebay elevation averaged 74.6’ to 75.9’ msl.  River temperature averaged 55 to 56° F.

  - Spill Bay 18 was closed at 1330 on 31 October for spill deflector work.  Bay 1 was opened 8” to provide additional adult attraction flow.  This translates into a daily spill average of 2.4kcfs.

  - Units 3 and 5 remain out of service for turbine rehab.  Unit 15 remains out of service for a 4-yr overhaul.  Station service Unit 0 returned to service at 1630 on 05 November.

  - Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly, if drawdown exceeds 1.0’.  At 1400 on 08 November, F2 was placed on standby to facilitate trashrack raking.  From 1424 until 1530 on 10 November, both Fish Units were placed on standby to float trash.

- ACTIVITIES.

  - AWS Closures.   The following dates and times are when the respective valves were closed for cleaning.

05 November- BI exit from 1548 until 1554

  - STS/VBS Inspections.  Four STSs were video inspected this reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 11/8 | 690 | okay |
| 12 | 11/8 | 695 | okay |
| 17 | 11/8 | 700 | okay |
| 18 | 11/8 | 710 | okay |

Table 1.  STS/VBS Inspection Data.

  - STS removal. PH1 STS remain OOS per NMFS request.

  - Dewatering and Fish Salvage.  Unit 15 tail logs were pulled on 06 November.  Biologists removed 13 catfish and two sculpin.

- RESEARCH.

  - WDFW Fish Counting.  24-hour video counts at BI and WA. Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - PSMFC Adult PIT.  Planning for construction at the Bradford Island and Cascade Island ladders continues.

  - WDFW Winter Steelhead tagging.  Tagging began 05 November.

4.  FISHWAYS.

  - Project biologists inspected 04 through 10 November this reporting week.  FPC inspected on 07 November.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | The velocity meter is not yet working. | Not fully installed. | Working on final installation. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers will be installed during winter maintenance. | 20013904 |
| All week | FG3-27 | Not in correct position for TW elev. | FG3-27 is open to replace FG3-28. | See above. |  |
| 11/4, 11/7, 11/9 | PH1 PCC velocity | Velocity meter registers <1.5 fps. | Water backs up in the channel. | Monitoring situation. |  |
| All week | Main Dam Avian wires | Wires removed. | Spillway deflector installation. | Grid to be replaced in Mid-April. |  |
| 11/4 | B-Branch entrances | Not in correct position for TW elev. | Entrance gates are operated manually. | Operators adjusted gates. |  |
| 11/5, 11/9-10 | Weir 37 | Reading >1.1’ | See misc. 5.3 | See misc. 5.3 |  |
| All week | Spill bay 18 | On seal | Spillway deflector installation. | Spill bay 1 opened 8”. |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 11/04 | 12.8 | 12.6 |
| 11/05 | 12.7 | 12.6 |
| 11/06 | 12.5 | 12.3 |
| 11/07 | 12.2 | 12.0 |
| 11/08 | 11.8 | 11.7 |
| 11/09 | 11.4 | 11.3 |
| 11/10 | 11.1 | 11.0 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 08 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.

  - The B-Branch and Cascade Island computers were installed.  Until sensors have been calibrated, entrance gates, diffusers, valves FV4-3, FV4-4, FV5-3, FV5-4 are operated in manual.

  - Weir 37 float control doesn’t adequately control water level over the weir.  A sonic transducer will be installed this winter, which should correct the problem.

  - Powerhouse Two Ice and Trash Chute was opened from 1412 until 1419 on 05 November.

  - Weir 37 was operated in manual from 1312 until 1339 on 05 November while the stillwell was cleaned.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//