### CENWP-OP-B                                                                                                                          20 November, 2001

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 46 of 2001, which covers the period 11 through 17 November.

- OPERATION SUMMARY.

  - Daily river flow averaged 87.4 to 112.8kcfs.  Daily project tailwater elevation averaged 7.8’ to 10.8’ msl.  Daily project forebay elevation averaged 73.7’ to 75.3’ msl.  River temperature averaged 53 to 54° F.

  - Spill Bay 18 was closed at 1330 on 31 October for spill deflector work.  Bay 1 was opened 8” to provide additional adult attraction flow.  This translates into a daily spill average of 2.4kcfs.

  - Units 3 and 5 remain out of service for turbine rehab.  Unit 15 returned to service at 2312 on 14 November then went out of service from 0654 until 1630 on 15 November because of a scroll case leak.  Unit 15 went out of service again from 1654 on 16 November until 0836 on 17 November because of a faulty speed switch.  Unit 17 was out of service from 0454 until 1312 on 14 November for governor repair.  Unit 9 and 10 were out of service from 0836 until 1354 and from 0930 until 1130, respectively, because of problems with core drilling for a new voltage regulator for Unit 9.

  - Second Powerhouse fish units remain in service.  They provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly, if drawdown exceeds 1.0’.  To facilitate trashrack raking on 15 November, F2 went to standby from 0735 until 0802.  F1 went to standby from 0804 until 0840.

- ACTIVITIES.

  - AWS Closures.   AWS valves were closed for trashrack cleaning as listed below.

13 November- FV3-7 from 0845 until 0920

FV5-9 from 0925 until 1010

FV6-9 from 1020 until 1030

FV1-1 from 1045 until 1100

15 November- FV1-1 from 1505 until 1544

  - STS/VBS Inspections.  No STSs were video inspected this reporting week.

  - STS removal. PH1 STS remain OOS per NMFS request.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities to report.

- RESEARCH.

  - WDFW Fish Counting.  24-hour video counts ongoing at BI and WA Shore ladders.

  - NMFS Saltwater rearing. The Saltwater rearing facility is in operation.  Sampling May- November.

  - PSMFC Adult PIT.  Planning for construction at the Bradford Island and Cascade Island ladders continues.

  - WDFW Winter Steelhead tagging.  Tagging began 05 November.

4.  FISHWAYS.

  - Project biologists inspected 11, 12, 14-17 November this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 collection channel electronic velocity meter. | The velocity meter is not yet working. | Not fully installed. | Working on final installation. |  |
| All week | FG3-28 | Out of service | Manually closed because of displaced diffuser valve cover. | New covers will be installed during winter maintenance. | 20013904 |
| All week | FG3-27 | Not in correct position for TW elev. | FG3-27 is open to replace FG3-28. | See above. |  |
| All week | Spill bay 18 | On seal | Spillway deflector installation. | Spill bay 1 opened 8”. |  |
| All week | Main Dam Avian wires | Wires removed. | Spillway deflector installation. | Grid to be replaced in Mid-April. |  |
| 11/11-12 | B-Branch and Cascade Island entrances | Not in correct position for TW elev. | Entrance gates are operated manually. | Operators adjusted gates. |  |
| 11/11-17 | Weir 37 | Reading >1.1’ | See misc. 5.3 | See misc. 5.3 |  |
| 11/11-12, 11/15-17 | PH1 PCC velocity | Velocity meter registers <1.5 fps. | Water backs up in the channel. | Monitoring situation. |  |
| 11/11 | FG3-3 | Not in correct position for TW elev. | Unknown | Operators informed |  |
| 11/14-16 | Bradford Island fishway staff gauges | Reading <1.0’ | Unknown | Operators informed |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 11/11 | 10.8 | 10.7 |
| 11/12 | 10.7 | 10.5 |
| 11/13 | 10.9 | 10.7 |
| 11/14 | 11.0 | 10.8 |
| 11/15 | 11.1 | 10.9 |
| 11/16 | 11.0 | 10.9 |
| 11/17 | 11.0 | 10.8 |

  - Sensor Calibration.  Water level sensors were checked for calibration on 14 November.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - Because of low tailwater elevations and the physical limits of the weir gates, entrance openings for PH1 Collection Channel are less than 8.0’.   Gate 64 has been reprogrammed to maintain at least an 8’ opening.

  - The B-Branch and Cascade Island computers were installed.  Until sensors have been calibrated, entrance gates, diffusers, valves FV4-3, FV4-4, FV5-3, FV5-4 are operated in manual.

  - Weir 37 float control doesn’t adequately control water level over the weir.  A sonic transducer will be installed this winter, which should correct the problem.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//