### CENWP-OP-B                                                                                                                           22 January, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 03 of 2002, which covers the period 13 through 19 January 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 128.1 to 196.6kcfs.  Daily project tailwater elevation averaged 12.9’ to 16.9’ msl.  Daily project forebay elevation averaged 72.9’ to 75.0’ msl.  River temperature averaged 44 to 46° F.  Daily turbidity averaged 4.5 to 7’ on the secchi disk.

  - Spill Bays 18 and 1 are closed for spill deflector work.

  - Units 3 and 5 remain out of service for turbine rehab.  Unit 17 remains out of service for VBS slot modification work.  Unit 1 went out of service from 1548 until 1800 on 13 January due to a ground in the control power.  Unit 15 was out of service from 0500 until 0930 on 15 January due to stuck wicket gates.  Unit 7 was out of service from 0918 until 1030 on 16 January for replacement of an oil flow switch.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly, if drawdown exceeds 1.0’.  F1 remains out of service for winter maintenance.  As coordinated with NMFS, F2 is supplying all attraction flow at this time. (see Misc. 5.4)

- ACTIVITIES.

  - AWS Closures. Bradford Island AWS valves closed for winter maintenance.

14 January- FV5-9 closed for cleaning from 0725 until 0735

14 January- FV6-9 closed for cleaning from 0745 until 0800

19 January- FV6-6 closed for cleaning from 1530 until 1545

19 January- FV5-9 closed for cleaning from 1600 until 1610

  - STS/VBS Inspections.  All STSs have been removed for winter maintenance.

  - Dewatering and Fish Salvage.  On 15 January, biologists removed 14 resident fishes (including peamouth, suckers, and whitefish) from Unit 3 tail logs.  On 16 January, biologists removed 1 stickleback from the bypass flume of the JMF.

- RESEARCH.

  - WDFW Fish Counting.  24-hour video count ongoing at the WA Shore ladder.

  - PSMFC Adult PIT.  Installation underway at Bradford Island ladder.

  - WDFW Winter Steelhead tagging.  Trapping continues three or four days a week.

  - NMFS Lamprey.  Tracking continues.  Plans for a trap in FV3-9 AWS channel underway.  More lamprey plates to be installed in the Washington Shore ladder in February.

4.  FISHWAYS.

  - Project biologists inspected 14, 16, and 18 January this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH2 electronic velocity meter. | Meter not yet working | Need new cable. | Will be installed in February. |  |
| All week | Weir 37 | Reading >1.0’ | Faulty sonic transducer. | See misc. 5.2. |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperature probes are out of service for calibration.

  - Sensor Calibration.  Calibration was not checked as there were no sensors in service this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - The B-Branch and Cascade Island computers were installed.  Until sensors have been calibrated, entrance gates, diffusers, valves FV4-3, FV4-4, FV5-3, FV5-4 are operated in manual.

  - Weir 37 float control doesn’t adequately control water level over the weir.  A sonic transducer will be installed this winter, which should correct the problem.

  - To aid spawning Chum below Bonneville, a minimum tailwater restriction of 11.4’ went into effect at 1054 on 28 November.  The restriction will continue until further notice.

  - As coordinated with NMFS, the ITC will not be used for AWS water.  F2 is being operated to maintain a 1.5’ differential.  In an effort to reduce the debris load during daylight hours, the fish unit is put on standby from 1800 until 0500 to float trash.

  - DSM2 and the JMF were dewatered on 15 January.  Biologists inspected the transport pipe on 16 January.   Some gouges were found below the water line inside the pipe.  Gouges measured approximately 3 inches long and ¼ inch deep.  Project investigating filling methods.  The pipe also showed evidence of compression.  Portland District engineers are investigating.

  - PH1 ITS was closed during the day on 14-15 January for work in the forebay and on 16 January for the PCC dive.

  - PH2 ITC was opened from 1630 until 1700 on 19 January to remove debris.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//