### CENWP-OP-B                                                                                                                                  01 May, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 17 of 2002, which covers the period 21through 27 April 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 242.2 to 301.8kcfs.  Daily project tailwater elevation averaged 19.2’ to 22.7’ msl.  Daily project forebay elevation averaged 75.5’ to 76.2’ msl.  River temperature averaged 48 to 50° F.  Daily turbidity measured 2.0 to 3.2’ on the secchi disk.

  - Spill Bays 1and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and are included in the new spill pattern.  Spill averaged 98.9 to 149.0kcfs for the week.

  - Unit 1 remains out of service for digital governor installation.  Unit 5 remains out of service for turbine rehab.  Units 6 and 7 were out of service from 0406 on 23 April until 1724 on 25 April for relay work .  Unit 8 went out of service at 0230 on 22 April for digital governor and exciter work.  Unit 10 was out of service from 1436 until 1648 on 24 April due to exciter control problems and from 0830 until 1330 on 25 April for a brush inspection.  Unit 17 was out of service for FGE testing from about 1645 until 2300 during the week.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 24 April.

- ACTIVITIES.

  - AWS Closures.  The following exits and AWS valves were closed for cleaning.

23 April- Bradford Island exit from 1523 until 1535

25 April- FV1-1 from 0906 until 0923

  - STS/VBS Inspections.  The following STSs/VBSs were inspected.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 01 | 3/02 | 284 | OUT OF SERVICE |
| 02 | 4/23 | 456 |  |
| 03 | 4/23 | 503 |  |
| 04 | 4/23 | 832 |  |
| 05 |  |  | OUT OF SERVICE |
| 06 | 4/23 | 802 |  |
| 07 | 4/22 | 75 |  |
| 08 | 2/27 | 778 |  |
| 09 | 4/22 | 543 |  |
| 10 | 3/02 | 48 |  |

Table 1.  STS Inspection Dates.

  - Dewatering and Fish Salvage.  DSM1 was turned south at 1000 on 23 April to repair damage resulting from the small trash sweep failure.  1 adult spring Chinook, 1 adult steelhead, 14 juvenile steelhead and 10 juvenile Chinook were removed and released downstream.

- RESEARCH.

  - CRITFC Age and Length Composition. Collected 120 Spring Chinook.  They will be collecting Chinook and Coho twice a week from 1 April to 31 October.

  - NMFS FGE.  Unit 17 FGE study is underway.

  - NMFS Lamprey.  Tracking continues.   Collection begins in June.

  - NMFS Saltwater Rearing.   200 yearling Chinook are collected from barges every other day, equaling 1109 fish to date.  Half are introduced to the seawater for long term rearing; the other half will be transported to Newport for the Vibrio challenge on 7 May.  PIT tagged Rapid River Hatchery fish have been detected.  Those fish that have passed through only Bonneville’s JBS or Bonneville and 2-5 other JBS’s will rear in seawater, all others will be released back to the river.

  - Normandeau Balloon-tag at Spillway.  Scheduled for 1-23 May and 1-15 August.

  - OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - ODFW Pikeminnow Electroshocking.  Part of northern pikeminnow management program.  Capturing and collecting biological data from pikeminnow, smallmouth bass, and walleye in Bonneville’s BRZ.  Electroshocking  1-5 April and 22-26 April.

  - Pelfrey Sturgeon Hatchery.  Scheduled to begin capturing broodstock in late May.

  - PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

  - PSMFC JMF.  Debris loads were heavy this week requiring almost constant attention and debris removal.  The screen cleaner cycled 4 times per hour.  The following fish were found stranded on the separator bars: 6 smolts, 9 kelts (released alive) and 3 kelts arrived dead.  Fallbacks recorded crossing the separator bars included: 187 steelhead, 89 salmon, and 83 unknown salmonids. 1,536 smolts were observed sliding across the separator bars.

  - PSMFC/NMFS Juvenile PIT.  Sampling and flat plate operations were interrupted Wednesday, 17 April and Tuesday, 23 April.  See Misc. 5.3.

  - U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur May-June.  May add separation–by-code study June-August.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - USGS Juvenile Radio tracking.  Study in progress.

  - USGS MGR.  Equipment installation continues.

  - USGS EMG studies.  Tissue samples will be taken from 200 Chinook starting 1 April through June.

  - USGS Lamprey.  Collection begins on 6 May.

  - USGS Sort by Code.   Fish lengths and weights are taken by NMFS’ Saltwater rearing crew and released back to the river.

  - WDFW Fish Counting.  16-hour visual and 8-hour video counts continue at Bradford Island and Washington Shore ladders.

  - WDFW Jaw tagging.  Tagging 50-75 fish per week, starting 1 April.

  - WDFW Winter Steelhead Tagging.  Trapping and tagging of steelhead continues one day a week.

  - WES Spillway Deflector Testing.  WES will be monitoring water quality equipment to determine effectiveness of new flip lips.  Study began with initiation of spill on 10 April.

  - WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.

4.  FISHWAYS

  - Project biologists inspected 22-26 April this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| 4/22-26 | PH1 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown- the rest of the ladder is in criteria. | No action at this time. |  |
| 4/21, 4/27 |  | Biologists did not inspect 7 days/ week. | Personnel shortage. | Job advertised. |  |
| 4/23 | DSM1 | Out of service | Repairs from small trash sweep. | DSM turned south. See misc. 5.3 |  |
| 4/22-24 | Cascade Island | Diffusers not in proper position for TW elevation. | Computer system not yet fully functioning | Operators informed, adjusted diffusers. | #6475 |
| 4/23-24 | B-Branch | Diffusers not in proper position for TW elevation. | Computer system not yet fully functioning. | Operators informed, adjusted diffusers. | #6474 |
| 4/23-24 | South Monolith | Gates not at proper depth. | Unknown | Operators adjusted gates. SDE was placed in manual. |  |
| 4/22-23 | Orifice 11A-N | Closed | Bad proximity switch |  | #6476 |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.   The temperature is recorded every 15 seconds, averaged for each hour then averaged for the entire day.  Temperatures are in Fahrenheit.  Temperatures for this week will be included in next weeks report.

  - Sensor Calibration.  Calibration was checked on 25 April this reporting week.  Everything is within criteria.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - FV4-3, FV4-4, FV5-3, and FV5-4 are operated in manual until the computer system is up and running.  Calibration should be completed sometime in April.

  - River temperature is the temperature of the water in the scroll case of Unit 2.  This temperature is recorded every 6 hours (the FPP requires a reading three times a day).   The temperature probe was recalibrated on 26 April.

  - Sampling and flat plate operations were interrupted from 2130 on 17 April due to damage to the Flat Plate and small dewatering screen.   The DSM was turned south from 1000 until 1500 on 23 April to facilitate repairs.

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.  FFU is monitoring and recording their activity.

  - Turbulent flows from spillbays 1 and 18 enter the side entrance gates of Cascade Island and Bradfrod Island B-branch ladders, causing poor entrance conditions.  District hydraulic engineers are investigating the problem.  BON proposes bulkheading the side entrances.

  - PH1 ITS was closed for researcher equipment installation from 1547 until 1621 on 23 April and from 0835 until 0845, 1115 until 1146, and 1628 until 1648 on 24 April.

  - On 24 April, Hatchery Well H2 failed.  The problem has been turned over to District engineers.  ODFW may need to supplement existing well water supplies with water from Tanner Creek.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//