### CENWP-OP-B                                                                                                                                  20 May, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 20 of 2002, which covers the period 12 through 18 May 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 198.3 to 227.2kcfs.  Daily project tailwater elevation averaged 16.3’ to 18.1’ msl.  Daily project forebay elevation averaged 73.0’ to 76.4’ msl.  River temperature averaged 53 to 54° F.  Daily turbidity measured 4.0 to 7.0’ on the secchi disk.

  - Spill Bays 1and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 86.0 to 134.7kcfs for the week.

  - Unit Operation

    - Unit 2 remains out of service for digital governor and exciter work.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 8 returned to service at 1606 on 16 May.

    - Unit 15 went out of service at 1454 on 14 May until the VBSs are repaired (see misc. 5.4).

    - Unit 17 returned to service at 2300 on 14 May.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 15 May.

- ACTIVITIES.

  - AWS Closures.  The following AWS closures for cleaning were reported.

14 May- BI exit from 1515 until 1520

16 May- FV3-7 from 0655 until 0806

  - STS/VBS Inspections.  No STSs/VBSs  inspections this week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities this week.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 56 Spring Chinook this reporting week.

  - NMFS FGE.  Unit 17 FGE study is underway.   NO FGE test on 13 May because of VBS failures.

  - NMFS Lamprey.  Tracking continues.   Collection begins in June.

  - NMFS Saltwater Rearing.  200 yearling Chinook are collected from barges every other day.  PIT tagged Rapid River Hatchery fish that have passed through only Bonneville’s JBS or Bonneville and 2-5 other JBS’s will rear in seawater, all others will be released back to the river.

  - Normandeau Balloon-tag at Spillway.  Study to run 20 May – mid June and 1-15 August.

  - OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

  - ODFW Pikeminnow Electroshocking.  Completed.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - Pelfrey Sturgeon Hatchery.  Capturing broodstock May 24 – June 24.

  - PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

  - PSMFC JMF.  Debris loads were light this week.  The screen cleaner cycled 4 times per hour.  Two kelts were released from the separator bars.  237 steelhead, 64 salmon, and 7 unknown salmonids fallbacks were recorded.  778 smolts slid off the end of the separator bars.  107 smolts were examined for GBT.

  - PSMFC/NMFS Juvenile PIT.  Monitoring continues.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur May-June.  May add separation–by-code study June-August.

  - USGS EMG studies.  Tissue samples will be taken from 200 Chinook 1 April through June.

  - USGS Juvenile Radio tracking.  Study in progress.

  - USGS Lamprey.  Collection of lamprey at the AFF began in May.

  - USGS MGR.  Began 4 May, but low river flows are interrupting the study.

  - USGS Sort by Code.  Length and weight are recorded and fish are released back to the river.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

  - WDFW Jaw tagging.  Tagging 50-75 fish per week as control for tangle net study.

  - WDFW Winter Steelhead Tagging.  Trapping and tagging steelhead once a week.

  - WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.

  - WES Spillway Deflector Testing.  WES will monitor water quality equipment to determine effectiveness of new flip lips.  Study began with initiation of spill on 10 April.

4.  FISHWAYS

  - Project biologists inspected 13-15 May this reporting week.  NMFS and FPC inspected on 14 May.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown- the rest of the ladder is in criteria. | No action at this time. |  |
| 5/12, 5/16-18 |  | Biologists did not inspect 7 days/ week. | Personnel shortage. | Job advertised. |  |
| 5/15 | CI entrance | Entrance differential high. | Unknown | FV5-4 throttled down. |  |
| All week | DSM2 | Add in valve closed. | Gaps in VBSs at Unit 15 and 17. | Valve closed until VBSs are repaired (see misc. 5.4) |  |
| All week | B-Branch | FG3-25 | Broken shaft. | An adjacent diffuser is opened. |  |
| 5/15 | A and B branch | Water over weir >1.3’ | Adjusting for shad season. | FV3-9 adjusted. |  |
| 5/13, 5/15 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown- the rest of the ladder is in criteria. | No action at this time. |  |
| All week |  | Biologists did not check calibration of PH1 PCC. | Personnel shortage | Job advertised. |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius this week.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/12 | 11.4 | 11.3 |
| 5/13 | 11.5 | 11.5 |
| 5/14 | 11.4 | 11.5 |
| 5/15 | 11.7 | 11.6 |
| 5/16 | 11.9 | 11.9 |
| 5/17 | 12.1 | 12.1 |
| 5/18 | 12.3 | 12.3 |

  - Sensor Calibration.  Calibration was not checked this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are operated in manual mode until stillwells can be installed for the tailwater sensors.  Installation will wait until spill has concluded.

  - Turbulent flows from spillbays 1 and 18 enter the side entrance gates of Cascade Island and Bradford Island B-branch ladders, causing poor entrance conditions.  District hydraulic engineers are investigating the problem.  On 3 May, the structural crew installed a bulkhead in the side entrance at Cascade Island.  Entrance conditions improved.  CG funds will be used to build a bulkhead for Bradford Island B-branch.

  - Sea lions and harbor seals have been observed in the tailrace of both powerhouses and the spillway.  No action is being taken by the project to harass, harm, or otherwise annoy these animals.  FFU is monitoring and recording their activity.

  - An adult steelhead was seen behind the add in water bars in DSM2 on 08 May.  VBSs were immediately video inspected.  Upon dewatering U17 A-slot, the VBS was found to have crumpled in towards the scroll case.   VBSs from U15 will be moved to U17 so that FGE testing may continue.  U15 will be out of service until new VBSs are made for that unit.

  - Diffuser FG3-25 appears to have a broken shaft.  The diffuser is in manual at this time.  FG3-23 is currently being used as a replacement.

  - Water elevations were set for shad passage mode on 14 May.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//