### CENWP-OP-B                                                                                                                                  03 June, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 22 of 2002, which covers the period 26 May through 01 June 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 245.8 to 349.5kcfs.  Daily project tailwater elevation averaged 19.3’ to 25.0’ msl.  Daily project forebay elevation averaged 75.3’ to 76.1’ msl.  River temperature averaged 56 to 57° F.  Daily turbidity measured 3.0 to 5.3’ on the secchi disk.

  - Spill Bays 1and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 92.7 to 134.7kcfs for the week.

  - Unit Operation

    - Unit 2 remains out of service for digital governor and exciter work.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 9 remains out of service for digital governor work and a five year overhaul.

    - Unit 11 returned to service at 0730.

    - Unit 15 remains out of service until the VBSs are repaired

    - Unit 17 was out of service for VBS cleaning from 1524 until 1706 on 30 May and from 1536 until 1642 on 01 June.  Unit 17 was out of service for FGE testing 28-31 May.

    - Unit 18 went out of service from 1600 until 2054 on 28 May and from 1706 until 1800 on 30 May for research camera equipment installation and removal.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 29 May.

- ACTIVITIES.

  - AWS Closures.  No AWSs were closed for cleaning.

  - STS/VBS Inspections.  The following STS/VBSs were inspected this week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 3 | 5/30 | 835 |  |
| 4 | 5/31 | 514 |  |
| 6 | 5/30 | 480 |  |

Table 1.  STS Inspection Dates.

  - Dewatering and Fish Salvage.  No dewaterings or fish salvage activities this week.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 40 Spring Chinook this reporting week.

  - NMFS FGE.  Unit 17 FGE study is underway.

  - NMFS Lamprey.  Collection began with 2 lamprey on 28 May.

  - NMFS Saltwater Rearing.  Collection and rearing continue.

  - Normandeau Balloon-tag at Spillway.  High flow tests ended on 1 June.  Low flow study commences in  August.

  - OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - Pelfrey Sturgeon Hatchery.  Capturing broodstock May 24 – June 24.

  - PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

  - PSMFC JMF.  Two kelts (1 alive and 1 dead) were stranded on the separator bars.  339 adult steelhead, 70 adult salmonids, and 1,078 smolts slid over the separator bars.

  - PSMFC/NMFS Juvenile PIT.  Observed elevated descaling rates at DSM1.  See misc 5.4

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur May-June.  May add separation–by-code study June-August.

  - USGS EMG studies.  Tissue samples will be taken from 200 Chinook 1 April through June.

  - USGS Juvenile Radio tracking.  Study in progress.

  - USGS Lamprey.  Collection of lamprey at the AFF began in May.

  - USGS MGR.  Began 4 May, but low river flows are interrupting the study.

  - USGS Sort by Code.  Length and weight are recorded and fish are released back to the river.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

  - WDFW Jaw tagging.  Tagging finished.

  - WDFW Winter Steelhead Tagging.  Trapping and tagging steelhead once a week.

  - WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.

  - WES Spillway Deflector Testing.  WES will monitor water quality equipment to determine effectiveness of new flip lips.  Study began with initiation of spill on 10 April.

4.  FISHWAYS

  - Project biologists inspected 28-30 May this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown- the rest of the ladder is in criteria. | No action at this time. |  |
| 5/26-27, 5/31, 6/1 |  | Biologists did not inspect 7 days/ week. | Personnel shortage. | Job advertised. |  |
| 5/29 | PH1 PCC | OG#9 not at correct elevation. | Unknown. | Gate manually adjusted. |  |
| 5/30 | PH1 PCC | WG#1 not at correct elevation. | FV1-1 was closed. | Gate and FV1-1 adjusted correctly. |  |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Reaumurs this week.  This scale is named after the French scientist Rene Antoine Ferchault de Reaumur, a discoverer of fabricating steel from iron, artificial egg incubation and an authority on the natural history of insects.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 5/26 | 10.96 | 11.04 |
| 5/27 | 11.04 | 11.04 |
| 5/28 | 10.96 | 10.96 |
| 5/29 | 11.04 | 11.04 |
| 5/30 | 11.2 | 11.2 |
| 5/31 | 11.44 | 11.44 |
| 6/1 | 11.6 | 11.68 |

  - Sensor Calibration.  Calibration was checked on 29 May this reporting week.  Everything is within criteria.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are operated in manual mode until stillwells can be installed for the tailwater sensors.  Installation will wait until spill has concluded.

  - Turbulent flows from spillbays 1 and 18 enter the side entrance gates of Cascade Island and Bradford Island B-branch ladders, causing poor entrance conditions.  District hydraulic engineers are investigating the problem.  On 3 May, the structural crew installed a bulkhead in the side entrance at Cascade Island.  Entrance conditions improved.  CG funds will be used to build a bulkhead for Bradford Island B-branch.

  - Juvenile mortalities at the JMF continue to be an intermittent  problem.  Some fish were dead with no apparent injuries.  Others were injured, many decapitated.   A group of dead fish came through on 30 May which were curled up: head to tail.  PSMFC agreed to hold some of these fish to take digital photos of them and possibly send some out for necropsy.  DSM2 Orifices are flushing six times a day.

  - Pacific States reported that intermittent descaling persisted at DSM1 this week.  Orifices are flushing six times a day.  Screen inspections began.  If problem persists, we will try raking trashracks.

  - PH1 ITS was closed for debris removal from chain gate 10C on 29 May from 1037 until 1500.

  - DSM2 Add in returned to service at 1110 on 30 May.  Two juvenile salmonids were behind the add in bars.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//