### CENWP-OP-B                                                                                                                                  08 July, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 27 of 2002, which covers the period 30 June through 06 July 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 258.2 to 314.3kcfs.  Daily project tailwater elevation averaged 19.9’ to 23.8’ msl.  Daily project forebay elevation averaged 74.6’ to 75.8’ msl.  River temperature averaged 61 to 62° F.  Daily turbidity measured 3.0’ to 3.5’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 87.3 to 166.8kcfs.

  - Unit Operation

    - Unit 0 (station service) was out of service from 0730 until 1700 on 01 July for brush ring work and from 0248 until 1548 on 02 July for slip ring work.

    - Unit 1 remains out of service for turbine rehab.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 6 returned to service at 1200 on 02 July.

    - Unit 11 was out of service from 0712 until 1448 on 02 July for transducer work.

    - Unit 12 went out of service at 1143 on 03 July due to the gatewell camera getting caught on the STS frame in A-slot.  (See misc. 5.5)

    - Unit 17 was out of service for FGE testing from about 1600 until 2100 from 01-03 July.  VBSs were cleaned during swing shift on FGE test nights.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured every day for Unit 17 and on 03 July for the rest of the units.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed for cleaning this reporting week.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 100 Chinook and 150 Sockeye this reporting week.

  - NMFS FGE.  Unit 17 FGE study is ongoing.  Summer tests are expected to be complete by 12 July.

  - NMFS Lamprey.  77 fish were collected for the Warm Springs tribe.  The lamprey flume is in operation at the Bradford Island AWS channel.

  - NMFS Saltwater Rearing.  Collection and rearing continue.

  - Normandeau Balloon-tag at Spillway.  Low flow study commences in August.

  - OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

  - PSMFC JMF.  One dead kelt was removed from the separator bars.  Recorded as going over the bars were 46 steelhead, 27 salmon and 3 unknown salmonid fallbacks and 144 smolts.  Several thousand fish were diverted into the sort by code tanks on 20 June.  (See misc. 5.4)

  - PSMFC/NMFS Juvenile PIT.  100 sub yearling Chinook were examined for GBT this week.  Sampling was interrupted on 04 July due to an Add in gate failure.  (See misc. 5.7)

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur June-September.

  - USGS Juvenile Radio tracking.  Study in progress.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

  - WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.

  - WES Spillway Deflector Testing.  WES monitoring water quality equipment to determine effectiveness of new flip lips.  Study began with initiation of spill on 10 April.

  - Yakama Dam Angling.  YIN began angling for pikeminnows at Bonneville on 1 July.

4.  FISHWAYS

  - Project biologists inspected 01-04 July this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown | No action at this time. |  |
| All week | Main dam | Two avian wires broken. | Vandalism | No action taken at this time. |  |
| 6/30, 7/5, 7/6 |  | Biologists did not inspect 7 days/ week. | Personnel shortage. | Training a new employee. |  |
| 7/2 | DSM2 | Channel elevation low. | Forebay low | No action taken at this time. |  |
| 7/4-6 | DSM1 | Water levels out of criteria | Add in valve malfunction. | Channel turned south. See misc 5.7 | TR# 8209 |
| 7/6 | Unit 12 | Orifices 12A-S and C-S OOS | Mounting bolt broken. | Channel elevation in criteria, TR submitted. See misc. 5.8 | TR#8213 |

  - Fish Ladder Temperatures.  Temperatures are measured 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 6/30 | 17.4 | 17.4 |
| 7/01 | 17.6 | 17.6 |
| 7/02 | 17.8 | 17.8 |
| 7/03 | 17.7 | 17.7 |
| 7/04 | 17.7 | 17.7 |
| 7/05 | 17.6 | 17.6 |
| 7/06 | 17.7 | 17.7 |

  - Sensor Calibration.  Calibration was checked on 04 July this reporting week.  The south end of the collection channel appears to be a little out of calibration.  TR#8228 was submitted.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are operated in manual mode until stillwells can be installed for the tailwater sensors.  Installation will wait until spill has concluded.

  - Turbulent flows from spillbays 1 and 18 enter the side entrance gates of Cascade Island and Bradford Island B-branch ladders, causing poor entrance conditions.  District hydraulic engineers are investigating the problem.  On 3 May, the structural crew installed a bulkhead in the side entrance at Cascade Island.  Entrance conditions improved.  CG funds will be used to build a bulkhead for Bradford Island B-branch.

  - There has been some difficulty in maintaining an opening for fish at PH1 weir gate 1.  Electricians are exploring the possibility of reprogramming the gate such that it will open if there is less than a 6’ opening and not close if less than 8’.

  - On 30 June the 3-way rotating gate was found stuck in the sample position for about 25 minutes.  This resulted in thousands of fish being diverted into the west SbyC tank.  A work request was submitted to the mechanics on the morning of 01 July.  An abrasion point was discovered that may have contributed to the gate sticking in the sample position.  Adjustments were made and the gate operated normally through 02 July.  The air has since been shut off to allow for testing after a period of inactivity.  The gate should be fully operation by the next scheduled SbyC diversion on 09 July.

  - At 1143 on 03 July Unit 12 was forced out of service when the STS/VBS camera became stuck on the STS frame in U12 A-slot.  Divers will be in to remove the camera during the fishway dives on 08-09 July.

  - From 1140 until 1530 on 04 July, DSM2 screen cleaner #1 was out of service due to a broken brush arm chain.

  - At 1430 on 04 July the add in valve at DSM1 became clogged with debris.  The valve continued to cycle and attempt to back flush but to no avail.  Operators tried the air burst system but that too failed to clear the valve for any length of time.  In the interest of fish safety, it was decided that the channel should be turned south until repairs could be made the morning of 08 July.

  - At 1430 on 06 July, 12 A-S and C-S orifices were placed in manual and closed.  The mounting bolts that keep the valve shaft vertical was broken.  It was believed that orifice cycling would cause further damage.  Channel elevation remained in criteria.  Mechanics will repair on 08 July.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//