### CENWP-OP-B                                                                                                                                  22 July, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 29 of 2002, which covers the period 14 through 20 July 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 216.7 to 257.4kcfs.  Daily project tailwater elevation averaged 17.9’ to 19.8’ msl.  Daily project forebay elevation averaged 75.0’ to 75.8’ msl.  River temperature averaged 64 to 66° F.  Daily turbidity measured 3.0’ to 6.2’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 85.6 to 127.9kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 2 was out of service from 0630 on 15 July until 1630 on 17 July for digital governor work.

    - Unit 4 remains out of service for digital governor work.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 7 was out of service from 1430 until 1630 on 16 July for governor work and from 1330 until 1706 on 19 July because of a turbine bearing oil pump malfunction.

    - Unit 8 was out of service from 0800 until 0830 on 16 July for governor work.

    - Unit 10 was out of service from 0706 until 0854 on 18 July for governor work and from 1330 until 1918 on 19 July because of  an emergency shutdown.

    - Unit 12 remains out of service because of an exciter failure.

    - Unit 17 was out of service from 1030 on 15 July until 1330 on 19 July for STS/VBS work.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  F2 had reduced load from 1330 until 1700 on 17 July to facilitate trashrack raking.  Head exceeded FPP criteria.

  - Gatewell drawdowns were measured every day for Unit 17 and on 19 July for the rest of the units.

- ACTIVITIES.

  - AWS Closures.  The following AWS valves were closed;

16 July- FV5-9 from 0705 until 1445 for a sonic probe installation.

18 July- FV3-9 from 1455 until 1510 for cleaning.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  On 18 July, DSM1 was turned south.  No fish were found in the channel.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 80 Chinook and 19 Sockeye this reporting week.

  - NMFS Lamprey.  161 lamprey were collected for the Warm Springs Tribe this reporting week.  The lamprey flume is in operation at the Bradford Island AWS channel.  Collection and tracking continue.

  - NMFS Saltwater Rearing.  Collection and rearing continue.

  - Normandeau Balloon-tag at Spillway.  Low flow study commences in August.

  - OCFWRU Transportation Study.  Study of post-transportation migration and survival of juveniles to run 29 April through 14 July.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

  - PSMFC JMF.  Recorded as going over the bars were 10 steelhead, 5 salmon and 24 smolts.  500-750 fish were directed into the SbyC holding tank when the three way rotating gate malfunctioned.  (See misc. 5.3).

  - PSMFC/NMFS Juvenile PIT.  200 sub yearling Chinook were examined for GBT this week.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur June-September.

  - USGS Juvenile Radio tracking.  Study in progress.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

  - WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.

  - WES Spillway Deflector Testing.  WES monitoring water quality equipment to determine effectiveness of new flip lips.

  - Yakama Dam Angling.  YIN began angling for pikeminnows at Bonneville on 1 July.

4.  FISHWAYS

  - Project biologists inspected 15-19 July this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | PH1 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown | No action at this time. |  |
| All week | Main dam | Two avian wires broken. | Vandalism | Will be repaired this winter maintenance season. |  |
| 7/14, 7/20 |  | Biologists did not inspect 7 days/ week. | Personnel shortage. | Training a new employee. |  |
| 7/16-19 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown | TR submitted | #8497 |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 7/14 | 18.7 | 18.8 |
| 7/15 | 18.8 | 18.8 |
| 7/16 | 19.0 | 18.7 |
| 7/17 | 19.3 | 19.0 |
| 7/18 | 19.7 | 19.3 |
| 7/19 | 19.9 | 19.3 |
| 7/20 | 19.9 | 19.3 |

  - Sensor Calibration.  Calibration was checked on 15 July this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed

  - Turbulent flows from spillbay 18 enter the side entrance gate Bradford Island B-branch ladder, causing poor entrance conditions.  CG funds will be used to build a bulkhead for B-branch.

  - The JMF was diverted to bypass mode from 1045 until 1130 on 16 July to facilitate repairs to the three way rotating gate.  During this same time, electricians investigated reports of the gate rotating while the SbyC program was disabled earlier that morning.  No electrical problem could be found.

  - Because of control problems, FV5-9 was operated in manual from 1900 on 16 July until 1500 on 18 July.

  - On 17 July, unit priority at PH1 was modified from the FPP.  A 19 July teletype details the changes.

  - The small trash sweep in DSM1 broke at 1750 on 17 July.  From 1135 until 1435 on 18 July, the DSM was turned south to facilitate repairs to the trash sweep.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//