### CENWP-OP-B                                                                                                                                  28 July, 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 30 of 2002, which covers the period 21 through 27 July 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 169.3 to 232.2kcfs.  Daily project tailwater elevation averaged 14.7’ to 19.0’ msl.  Daily project forebay elevation averaged 74.8’ to 75.9’ msl.  River temperature averaged 67 to 68° F.  Daily turbidity measured 5.0’ to 7.5’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are operational and included in the spill pattern.  Spill averaged 91.5 to 164.6kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 3 was out of service from 0500 until 1700 for bank work.

    - Unit 4 returned to service at 0842 on 24 July.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 7 went out of service at 0530 on 24 July for a vibration inspection.

    - Unit 12 returned to service at 1806 on 22 July.

    - Unit 13 went out of service at 0500 on 26 July due to a governor power failure.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured every day for Unit 17 and on 24 July for the rest of the units.

- ACTIVITIES.

  - AWS Closures.  No AWS valves were closed.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities this week.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 50 Chinook and 3 Sockeye this reporting week.

  - NMFS Lamprey.  The lamprey flume is in operation at the Bradford Island AWS channel.  Collection and tracking continue.

  - NMFS Saltwater Rearing.  Collection and rearing continue.

  - Normandeau Balloon-tag at Spillway.  Low flow study commences in August.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 winter maintenance season.

  - PSMFC JMF.  Recorded as going over the bars were seven steelhead, 5 salmon and 15 smolts.

  - PSMFC/NMFS Juvenile PIT.  107 sub yearling Chinook were examined for GBT this week.  PIT tag interrogation and sampling concluded at 1600 on 23 July.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I Transportation Study.  Evaluation of physiological condition of river run v. barged Snake River juveniles to occur June-September.

  - USGS Juvenile Radio tracking.  Study in progress.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

  - WES/Battelle/Mevatech Juvenile Hydroacoustics.  Study in progress.

  - WES Spillway Deflector Testing.  WES monitoring water quality equipment to determine effectiveness of new flip lips.

  - Yakama Dam Angling.  YIN began angling for pikeminnows at Bonneville on 1 July.

4.  FISHWAYS

  - Project biologists inspected 22-26 July this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| 7/22-23, 7/25-26 | PH1 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown | No action at this time. |  |
| All week | Main dam | Two avian wires broken. | Vandalism | Will be repaired this winter maintenance season. |  |
| 7/21, 7/27 |  | Biologists did not inspect 7 days/ week. | Personnel shortage. | Training a new employee. |  |
| 7/25-26 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Unknown | TR submitted | #8497 |
| 7/25-26 | B-Branch and Cascade Island | Entrance gates not in position for TW elev. | System is still in manual. | Operators adjusted gates accordingly. |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 7/21 | 20.1 | 19.6 |
| 7/22 | 20.4 | 19.9 |
| 7/23 | 20.7 | 20.1 |
| 7/24 | 20.8 | 20.1 |
| 7/25 | 20.9 | 19.9 |
| 7/26 | 20.7 | 19.6 |
| 7/27 | 20.4 | 19.7 |

  - Sensor Calibration.  Calibration was checked on 26 July this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed

  - Turbulent flows from spillbay 18 enter the side entrance gate Bradford Island B-branch ladder, causing poor entrance conditions.  CG funds will be used to build a bulkhead for B-branch.

  - On 17 July, unit priority at PH1 was modified from the FPP.  A 19 July teletype details the changes.  STSs were removed from Units 3-7 on 22-23 July.  PH1 priority is modified accordingly.

  - DSM1 is scheduled to turn south the morning of 29 July.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//