### CENWP-OP-B                                                                                                                            09 September 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 36 of 2002, which covers the period 01 through 07 September 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 95.3 to 123.7kcfs.  Daily project tailwater elevation averaged 9.4’ to 10.8’ msl.  Daily project forebay elevation averaged 75.2’ to 75.8’ msl.  River temperature averaged 66 to 67° F.  Daily turbidity measured 2.0’ to 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, will be open 4” during daylight hours.  Spill averaged 2.0 to 1.6kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 9 went out of service at 0924 on 03 September for an overhaul.

    - Unit 15 went out of service at 2024 on 04 September because of oil leaking from the north servo motor.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 04 September.

- ACTIVITIES.

  - AWS Closures.  No AWS closures this reporting week.

  - STS/VBS Inspections. No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  Biologists removed two sturgeon and one lamprey from Unit 9 draft tube on 03 September.  All fish were in good condition.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 101 chinook and four coho this reporting week.

  - NMFS Lamprey.  The Bradford Island AWS channel lamprey flume is in operation.  Tracking continues.

  - NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC/NMFS Adult PIT.  Detectors are installed in all ladders.  Some of the detectors have developed leaks and will be monitored throughout the season.  Repairs are scheduled for 2002-03 maintenance season.

  - PSMFC JMF.  One steelhead and two salmon were recorded as fallback over the separator bars.

  - PSMFC/NMFS Juvenile PIT.  DSM1 flow is running south.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I lamprey testing.  The AFF lamprey flume is in operation.  Tests ongoing.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

4.  FISHWAYS

  - Project biologists inspected 01-07 September this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | Main dam | Two avian wires broken. | Vandalism | Will be repaired this winter. |  |
| 9/01-5, 9/7 | Weir 37 | Reading >1.0’ | In manual | Stillwell to be installed this winter. Operators to adjust. |  |
| 9/2 | UMT staff gauge | Reading >1.0’ | Unknown | Operators to adjust |  |
| 9/1 | A and B branches | Reading <1.0’ | Unknown | Operators to adjust. |  |
| 9/5-7 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Low tailwater causes an inaccurate reading. | Sensor relocation this winter. |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 9/01 | 20.5 | 20.6 |
| 9/02 | 20.6 | 20.7 |
| 9/03 | 20.5 | 20.6 |
| 9/04 | 20.4 | 20.4 |
| 9/05 | 20.2 | 20.3 |
| 9/06 | 20.0 | 20.1 |
| 9/07 | 19.7 | 19.8 |

  - Sensor Calibration.  Checked calibration on 04 September this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

  - Turbulent flows from spillbay 18 enter the side entrance gate of Bradford Island B-branch ladder, causing poor entrance conditions.  CG funds will be used to build a bulkhead for B-branch.

  - During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.

  - The digital temperature probe at the AFF appears to be out of calibration.  We cannot recalibrate it until the lab is dewatered this winter.

  - Until a new drive shaft can be installed in the PDS screen cleaner, the screen will be cleaned manually.

  - On 29 August, chain gate 10C was closed for PH1 crane rail work.  Per NMFS request, chain gate 6B has been opened to substitute for 10C.  We will open 6B when middle units are operating and 1B when end units are operating.

  - Due to high numbers of fall chinook, the south picket leads at the AFF have been raised in the afternoon.  On 04 September leads 1-2 were raised at 1440, on 05 September lead 1 was raised at 1205, on 06 September lead 1 was raised at 1200, and on 07 September leads 1-4 were raised at 1305.

  - On 06 September, Unit 15 dewatering was halted when it was discovered that oil from the unwatering pump was discharging into the ice and trash chute.  Oil booms were deployed inside the chute and in the tailrace below the ITC.  By 1130, the top two tail logs were pulled and Unit 15 went back to tailwater.

DEBORAH L. CHENOWETH

# Operations Project Manager

//S//