### CENWP-OP-B                                                                                                                            23 September 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 38 of 2002, which covers the period 15 through 21 September 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 80.1 to 120.2 kcfs.  Daily project tailwater elevation averaged 7.8’ to 11.1’ msl.  Daily project forebay elevation averaged 75.5’ to 75.9’ msl.  River temperature averaged 64 to 66° F.  Daily turbidity measured between 5.0’ and 7.5’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged 2.0 to 2.2 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 9 remains out of service for an overhaul.

    - Unit 11 was out of service from 1330 until 1600 on 16 September for STS installation.

    - Unit 17 was out of service from 1618 18 September until 1515 19 September due to a servo oil leak.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  F1 was out of service from 1936 until 2242 on 18 September to facilitate instrumentation installation.

  - Gatewell drawdowns were measured on 18 September.

- ACTIVITIES.

  - AWS Closures.  No AWS closures this reporting week

  - STS/VBS Inspections.  No STS/VBSs  inspections this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 86 chinook and 50 coho this reporting week.

  - NMFS Lamprey.  The Bradford Island AWS channel lamprey flume is in operation.  Tracking continues.

  - NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC/NMFS Adult PIT.  Detectors have been installed in all ladders, some have developed leaks.  Repairs are scheduled for 2002-03 maintenance season.  Researchers tagged fish on 16 and 17 September.

  - PSMFC JMF.  Seven salmon and one unknown salmonid were recorded as fallback over the separator bars.

  - PSMFC/NMFS Juvenile PIT.  DSM1 flow is running south.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I lamprey testing.  The AFF lamprey flume is in operation.  Tests ongoing.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

4.  FISHWAYS

  - Project biologists inspected 15-21 September this reporting week.  NMFS inspected on 19 September.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | Main dam, PH2 | Avian wires broken or removed | Vandalism at main dam. PH2 Corner collector construction. | Will be repaired this winter. |  |
| 9/18 | Weir 37 | Reading >1.0’ | In manual | Stillwell to be installed in winter. |  |
| 9/15, 9/17-18, 9/20-21 | PH1 PCC velocity | Velocity <1.5 fps on electronic meter. | Unknown | No action taken. |  |
| 9/18 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Low TW causes an inaccurate reading. | Sensor relocation this winter. |  |
| 9/18-19 | UMT staff gauge | Reading <1.0’ over the weir. | Unknown | Operators adjusted FV5-9. |  |
| 9/20 | A branch | Reading <1.0’ over the weir. | Unknown | Operators to adjust FV3-9 |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 9/15 | 20.1 | 20.1 |
| 9/16 | 19.8 | 19.9 |
| 9/17 | 19.6 | 19.6 |
| 9/18 | 19.3 | 19.3 |
| 9/19 | 19.1 | 19.1 |
| 9/20 | 19.0 | 18.9 |
| 9/21 | 18.9 | 18.8 |

  - Sensor Calibration.  Checked calibration on 17 September this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

  - During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.

  - During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

  - Until a new drive shaft can be installed in the PDS screen cleaner, the screen will be cleaned manually.

  - At 1242 on 12 September FPOM requested two units to operate at PH1 during daylight hours.  This operation is intended to split flow and migrating adults between the two powerhouses.  Units 2 and 3 are in operation.  A teletype, dated 9/12/2002 was issued detailing this operation.

  - 3D cam testing took place at PH2 this week.  PH1 will be tested next week.

  - FV3-7 has not been controlling properly.  Operators switched it to manual.  An electrician is working on it.

  - Avian wires were removed on the morning of 20 September to facilitate contract work for the B2 Corner Collector.

JAMES R. MAHAR

# Operations Manager

//S//