### CENWP-OP-B                                                                                                                            30 September 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 39 of 2002, which covers the period 22 through 28 September 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 95.9 to 138.3 kcfs.  Daily project tailwater elevation averaged 9.3’ to 12.3’ msl.  Daily project forebay elevation averaged 75.5’ to 75.7’ msl.  River temperature averaged 64° F.  Daily turbidity measured between 6.0’ and 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged 2.1 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 2 was out of service from 0524 until 1300 on 24 September due to loss of governor PLC.

    - Unit 3 was out of service from 0800 until 1524 on 24 September for governor testing.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 8 was forced out of service at 0812 on 23 September due to the inability to deploy headgates.

    - Unit 9 remains out of service for an overhaul.

    - Unit 10 was forced out of service at 0812 on 23 September due to the inability to deploy headgates.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 25 September.

- ACTIVITIES.

  - AWS Closures.  The following AWS closures occurred this reporting week.

23 September- FV1-1 closed for cleaning from 1325 until 1400

26 September- FV3-7 closed for cleaning from 1000 until 1040

26 September- FV1-1 closed for cleaning from 1530 until 1610

  - STS/VBS Inspections.  No STS/VBSs  inspections this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 60 chinook and 50 coho this reporting week.

  - NMFS Lamprey.  The Bradford Island AWS channel lamprey flume was removed on 26 September.  Tracking will continue.

  - NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC/NMFS Adult PIT.  Detectors have been installed in all ladders, some have developed leaks.  Repairs are scheduled for 2002-03 maintenance season.  Researchers tagged fish on 26 and 27 September.

  - PSMFC JMF.  One steelhead and nine salmon were recorded as fallback over the separator bars.

  - PSMFC/NMFS Juvenile PIT.  DSM1 flow is running south.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week until October.

  - U of I lamprey testing.  The AFF lamprey flume is in operation.  Tests ongoing.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

4.  FISHWAYS

  - Project biologists inspected 22-28 September this reporting week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | Main dam, PH2 | Avian wires broken or removed | Vandalism at main dam. See misc. 5.7 | Will be repaired this winter. |  |
| 9/22-23, 9/25-26 | Weir 37 | Reading >1.0’ | In manual | Stillwell to be installed in winter. |  |
| 9/22-24, 9/26-28 | PH1 PCC velocity | Velocity <1.5 fps on electronic meter. | Unknown | No action taken. |  |
| 9/23,9/25, 9/27-28 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Low TW causes an inaccurate reading. | Sensor relocation this winter. |  |
| 9/24-28 | CI diffusers | Not in correct position for TW elev. | Ladders are in manual. | Stillwells to be installed in winter. |  |
| 9/24-26, 9/28 | B branch diffusers. | Not in correct position for TW elev. | Ladders are in manual. | Stillwell to be installed in winter. |  |
| 9/24 | A & B branches | Reading <1.0’ over the weir. | Unknown | Operators to adjust FV3-9 |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 9/22 | 18.7 | 18.6 |
| 9/23 | 18.7 | 18.7 |
| 9/24 | 19.1 | 19.0 |
| 9/25 | 19.2 | 19.2 |
| 9/26 | 19.1 | 19.1 |
| 9/27 | 19.0 | 19.1 |
| 9/28 | 18.9 | 19.0 |

  - Sensor Calibration.  Checked calibration on 22 September this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

  - During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.

  - During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

  - Until a new drive shaft can be installed in the PDS screen cleaner, the screen will be cleaned manually.

  - Units 2 and 3 are no longer operated to split flow and migrating adults between the two powerhouses.  Priority has been switched back to PH2.

  - Governor testing took place at PH1 this week.

  - Avian wires were removed on the morning of 20 September to facilitate contract work for the B2 Corner Collector.

  - As of 23 September, Units 8 and 10 are out of service due to the inability to deploy headgates during the crane rail construction.

  - DSM2 screen cleaner #1 returned to service at 0830 on 24 September.  It had been out of service since 20 September due to a broken chain.

JAMES R. MAHAR

# Operations Manager

//S//