### CENWP-OP-B                                                                                                                                      14 October 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 41 of 2002, which covers the period 06 through 12 October 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 83.7 to 127.6 kcfs.  Daily project tailwater elevation averaged 8.3’ to 12.1’ msl.  Daily project forebay elevation averaged 74.6’ to 75.4’ msl.  River temperature averaged 61 to 59° F.  Daily turbidity measured 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged. 2.0 to 2.1 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 7 remains forced out of service for crane rail work.

    - Unit 8 remains forced out of service for crane rail work.

    - Unit 9 remains out of service for an overhaul.

    - Unit 10 was remains forced out of service for crane rail work.

    - Unit 16 went out of service at 0848 on 07 October for a four year overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 09 October.

- ACTIVITIES.

  - AWS Closures.  No AWS closures occurred this reporting week:

  - STS/VBS Inspections.  The following STS/VBSs were inspected last reporting week.

| #### Unit | #### Date | #### Run Hours | #### Comments |
| --- | --- | --- | --- |
| 11 | 9/30 | 494 | B-slot belt not running. Replaced with STS #3 |
| 12 | 10/1 | 433 |  |
| 13 | 10/2 | 432 |  |
| 14 | 10/2 | 447 |  |
| 15 | 10/2 | 594 |  |
| 16 | 10/2 | 626 |  |
| 17 | 10/2 | 698 |  |
| 18 | 10/2 | 673 |  |

Table 1.  STS Inspection Dates.

  - Dewatering and Fish Salvage.  Biologists removed 12 sturgeon, three channel catfish, one sculpin, and one sucker from Unit 16 draft tube on 08 October.  All fish were released downstream

- RESEARCH.

  - CRITFC Age and Length Composition.  Collected 33 chinook and 50 coho this reporting week.

  - NMFS Lamprey.  Tracking continues.

  - NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath.

  - ODFW Summer Steelhead sampling.  Sampling 2 days/week 8 hours/day.  Will sample 1% of the run.

  - PSMFC/NMFS Adult PIT.  Detectors have been installed in all ladders, some have developed leaks.  Repairs are scheduled for 2002-03 maintenance season.

  - PSMFC JMF.  Three steelhead and two salmon were recorded as fallback over the separator bars.

  - U of I Adult Radio tracking.  Trapping began 1 April and will continue 7 days/week into October.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

4.  FISHWAYS

  - Project biologists inspected 06 through 12 October this week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | Main dam, PH2 | Avian wires broken or removed | Vandalism and BCC work. | Will be repaired this winter. |  |
| 10/9-12 | PH1 PCC velocity | Velocity <1.5 fps on electronic meter. | Unknown | No action taken. |  |
| 10/9-11 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Low TW causes an inaccurate reading. | Sensor relocation this winter. |  |
| 10/6 | Weir 37 | Reading > 1.0’ | In manual | Stillwell to be installed this winter. |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 10/06 | 17.0 | 17.0 |
| 10/07 | 16.9 | 16.9 |
| 10/08 | 16.9 | 16.9 |
| 10/09 | 16.9 | 16.9 |
| 10/10 | 16.6 | 16.6 |
| 10/11 | 16.3 | 16.3 |
| 10/12 | 15.7 | 15.8 |

  - Sensor Calibration.  Checked calibration on 09 October this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

  - During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.

  - During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

  - Repairing the PDS screen cleaner requires the JMF go to bypass.  The screen will be cleaned manually until the end of the season (31 October).

  - As of 30 September, Units 7, 8 and 10 are out of service due to the inability to deploy headgates during the crane rail construction.

  - Due to alarm problems, FV6-9 went to manual and closed at 0110 on 12 October.

  - PH2 ice and trash chute was open from 1015 until 1935 on 07 October.  It was left open to clear trash from the forebay at 1000 on 08 October.

  - PH1 entrance gates were closed from 0530 until 1600 on 10 October.  The closure allowed District engineers to measure flows in the collection channel.  The closure was coordinated with the agencies.

JAMES R. MAHAR

# Operations Manager

//S//