### CENWP-OP-B                                                                                                                                      29 October 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 43 of 2002, which covers the period 20 through 26 October 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 77.2 to 121.1 kcfs.  Daily project tailwater elevation averaged 7.7’ to 11.2’ msl.  Daily project forebay elevation averaged 74.5’ to 75.4’ msl.  River temperature averaged 56 to 57° F.  Daily turbidity measured 6.5 to 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are open 6” during daylight hours.  Spill averaged. 2.1 kcfs.

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 5 remains out of service for turbine rehab.

    - Unit 7 remains forced out of service for crane rail work.

    - Unit 8 remains forced out of service for crane rail work.

    - Unit 9 remains out of service for an overhaul.

    - Unit 10 remains forced out of service for crane rail work.

    - Unit 16 remains out of service for an overhaul.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.

  - Gatewell drawdowns were measured on 23 October.

- ACTIVITIES.

  - AWS Closures.  The following AWS closures occurred this reporting week.

FV1-1 closed for cleaning from 1500 until 1545 on 21 October.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No dewatering or fish salvage activities this reporting week.

- RESEARCH.

  - NMFS Lamprey.  Tracking continues.

  - NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath.

  - PSMFC/NMFS Adult PIT.  Detectors have been installed in all ladders, some have developed leaks.  Repairs are scheduled for 2002-03 maintenance season.

  - PSMFC JMF.  Four salmon and one unknown salmonid were recorded as fallback over the separator bars.  Monitoring will conclude at 0700 on 31 October.

  - WDFW Fish Counting.  16-hr visual and 8-hr video counts at Bradford Island and Washington Shore.

4.  FISHWAYS

  - Project biologists inspected 20 through 26 October this week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | Main dam, PH2 | Avian wires broken or removed | Vandalism and BCC work. | Will be repaired this winter. |  |
| All week | DSM 1 | Orifice lights out for more than 24 hours. | Crane rail contractors on site. | Operators to correct after hours. |  |
| 10/22, 10/24-26 | PH1 PCC velocity | Velocity <1.5 fps on electronic meter. | Unknown | No action taken. |  |
| 10/20, 10/25 | PH2 PCC velocity | Velocity <1.5fps on the electronic meter. | Low TW causes an inaccurate reading. | Sensor relocation this winter. |  |
| 10/24, 10/26 | Weir 38 | Reading > or < 1.0’ | Unknown |  |  |
| 10/22 | Bradford Island | Water over A and B branch >1.0’ | Forebay level change. | Operators to adjust. |  |
| 10/23 | B branch | Diffusers not correct for TW elev. | System in manual until stillwell is installed. | Operators to adjust. |  |

  - Fish Ladder Temperatures.  Measurements are taken 3 weirs down from the count station at Bradford Island and at the junction of the UMT and the main ladder at Washington shore.  Temperatures are in Celsius.

| Date | Wash. Shore | Bradford Is. |
| --- | --- | --- |
| 10/20 | 15.4 | 15.3 |
| 10/21 | 15.4 | 15.4 |
| 10/22 | 15.4 | 15.4 |
| 10/23 | 15.1 | 15.1 |
| 10/24 | 14.7 | 14.7 |
| 10/25 | 14.4 | 14.3 |
| 10/26 | 14.3 | 14.3 |

  - Sensor Calibration.  Checked calibration on 23 and 26 October this week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

  - During low tailwater, the PH2 monoliths are unable to maintain greater than 13’ openings.

  - During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

  - Repairing the PDS screen cleaner requires the JMF go to bypass.  The screen will be cleaned manually until the end of the season (31 October).

  - As of 30 September, Units 7, 8 and 10 are out of service due to the inability to deploy headgates during the crane rail construction.

  - FV6-9 went to manual at 0815 on 26 October due to excessive alarming.  The valve failed to control properly.  Maintenance crews will look at it on Monday.

JAMES R. MAHAR

# Operations Manager

//S//