### CENWP-OP-B                                                                                                                                  17 December 2002

MEMORANDUM FOR CENWP-OP, ATTN: Gary Johnson

SUBJECT: Bonneville Lock and Dam, Fishway and Fish Activities for week 50 of 2002, which covers the period 08 through 14 December 2002.

- OPERATION SUMMARY.

  - Daily river flow averaged 116.2 to 126.4 kcfs.  Daily project tailwater elevation averaged 11.5’ to 11.6’ msl.  Daily project forebay elevation averaged 72.4’ to 75.6’ msl.  River temperature averaged 45° F.  Daily turbidity measured 7.0’ on the secchi disk.

  - Spill Bays 1 and 18, which supply attraction flow for Cascades Island and Bradford Island ladders respectively, are now closed 24 hours.  Spill averaged 0.0 to 1.3 kcfs, the 1.3 came from the bay 18 being opened 6” from 0530 until 1900 on 14 December for adult attraction at Bradford Island (see Misc5_5).

  - Unit Operation

    - Unit 1 remains out of service for turbine rehab.

    - Unit 2 was out of service from 0530 until 1348 on 04 December for new power supply installation.

    - Unit 5 was out of service from 0700 until 1100 on 12 December to facilitate trashrack raking.

    - Unit 6 was out of service from 1100 until 1318 on 12 December to facilitate trashrack raking.

    - Unit 7 was out of service from 0700 on 10 December until 1630 on 11 December for crane rail work and fyke net frame removal.

    - Unit 8 was out of service from 0700 on 10 December until 1630 on 11 December for crane rail work and fyke net frame removal.

    - Unit 9 was out of service from 0700 on 10 December until 1630 on 11 December for crane rail work and fyke net frame removal.

    - Unit 10 was out of service from 0700 on 10 December until 1630 on 11 December for crane rail work and fyke net frame removal.

    - Units 11 and 12 were out of service for B2 corner collector dive operations from about 0500 until 1730 from 12-13 December and from 0700 until 1000 on 14 December.

    - Unit 15 was out of service from 0518 until 1630 on 13 December due to a transformer problem.

    - Unit 16 remains out of service for an overhaul.

    - Units 17 was out of service from 0518 until 1630 on 13 December due to a transformer problem.

  - Second Powerhouse fish units provide attraction flow for the Washington Shore fish ladder.  The units are placed on standby from approximately 0000-0300 nightly if drawdown exceeds 1.0’.  Fish Unit 1 remains out of service for overhaul and stator rewind.  F2 is on standby until it comes out of service the 16th of December.  F2 was out of service from 0518 until 1630 on 13 December due to a transformer problem.

  - Gatewell drawdowns are measured on Wednesdays.

- ACTIVITIES.

  - AWS Closures.  The following AWS valves were closed for cleaning.

09 December- FV1-1 from 0750 until 0805

FV3-9 from 0820 until 0825

10 December- FV1-1 from 1045 until 1110

FV1-1 from 2005 until 0200 11 December to float debris.

12 December- FV1-1 from 1150 until 1210

13 December- FV5-3 and FV5-4 closed from 0840 until 1200 to change bulkheads.

FV1-1 from 1500 until 1520

14 December- FV5-9 closed at 1355.  Cascade Island to orifice flow.

  - STS/VBS Inspections.  No STS/VBSs were inspected this reporting week.

  - Dewatering and Fish Salvage.  No fish salvage or dewatering activities this reporting week.

- RESEARCH.

  - NMFS Lamprey.  Tracking continues.

  - NMFS Saltwater Rearing.  Rearing continues.  Specific data available from Lyle Gilbreath.

  - WDFW Fish Counting.  24-hr video counts at Bradford Island and Cascade Island.

4.  FISHWAYS

  - Project biologists inspected 09-13 December this week.

  - Fish Passage Plan Observations.

| DATE | ##### LOCATion | ##### FPP Deviation | ##### CAUSE | ##### RESPONSE | ##### TR/WAR |
| --- | --- | --- | --- | --- | --- |
| All week | Main dam, PH1, PH2 | Avian wires broken or removed | Vandalism and contractor work. | Will be repaired this winter. |  |
| All week | PH1 PCC velocity | Velocity <1.5 fps on electronic meter. | Unknown | No action taken. |  |
|  |  | Calibration not checked. |  |  |  |

  - Fish Ladder Temperatures.  Temperatures are not recorded in the winter.

  - Sensor Calibration.  Calibration was not checked this reporting week.

  - Zebra Mussel Monitoring.  No signs of colonization were observed this reporting week.

- MISCELLANEOUS

  - B-branch and Cascade Island are in manual mode until tailwater stillwells can be installed this winter.

  - During low tailwater, the PH1 weir gates are unable to maintain greater than 8’ openings.

  - As of 13 November, and until further notice, the Project has a hard constraint tailwater elevation no less than 11.3’ msl during all hours and a soft constraint of 11.3’-11.7’msl between 0700-1900 hours.  This is for the protection of the chum redds around Ives Island.

  - On 10 December, PH1 fyke net frame was removed.

  - A teletype was mistakenly interpreted to indicate that the spillbay adjacent to BI ladder should be opened when Cascades Island was taken out of service.   They bay is now closed.

JAMES R. MAHAR

# Operations Manager

//S//